## RDM Org
ROOM DATA MATRIX |  |  |  |  | INTERIOR CONSTRUCTION | [8 empty] | DOORS AND HARDWARE | [6 empty] | MECHANICAL | [9 empty] | ELECTRICAL | [6 empty] | IT
[5 empty] | FLOOR |  | WALLS |  |  |  | CEILING |  | NOTES | [7 empty] | Note: Use parameters within FGI Guidelines for the noted FGI Equivalent category, unless noted otherwise. | [9 empty] | POWER |  |  | LIGHTING
DEPARTMENT | ROOM NAME | ROOM NAMES (VA) | FGI EQUIVALENT FOR ASHRAE 170 | FGI EQUIVALENT FOR TABLE 1.2-5 Minimum Sound Isolation | Floor Finish | Base | Wall Finish | Wainscot Material | Wainscot Height | STC | Ceiling Finish | Height | Notes | Size (Width) | Type | Material | Glazing | Rating | Hardware Group | Hardware Notes | Indoor Temperature Cooling F | Indoor Temperature Heating F | Indoor Relative Humidity % RH Max | Indoor Relative Humidity % RH Min | Minimum Total ACH | Minimum OA ACH | Room Air Return Gen. Exh G Spec Exh S | Maximum Noise Level NC | Room Air Balance | HVAC Notes | # Duplex Receptacles | # Quad Receptacles | Power - Notes | Fixture Type | Controls | Lighting - Special Requirements | Lighting - Notes | # Data Outlets (standard density WAO)
General Rooms/Spaces | Exam Room | PACT Exam | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 10 | 3'-0" --------------- 3'-6" | Flush | Wood | _ | _ | 12 SE | 3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 8 | 1 |  |  | Multilevel Switching, Dimming & Occupancy | Multi-level switching or manual dimming | N/A | 3
General Rooms/Spaces | Exam Room | Exam Room - Multi-Specialty, Exam / Treatment, Exam - Consult, Consult Room - PACT, Exam/Consult Room (Mental Health/Social Work), Exam Room EMG/EEG, Exam Room-Cardiology, Exam/Consult, Nurse Practitioner, Women's Health Exam, Tele-Health Exam, Optometry Exam Treatment Room, Eye Lane, Tele-Retinal, TECHS, Applicance Fitting Room, Fitting Room, Physical Therapy Room, Occupational Treatment Room | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 10 | 3'-6" | Flush | Wood | _ | _ | 12 S |  | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | 8 | 1 |  |  | Multilevel Switching, Dimming & Occupancy | Multi-level switching or manual dimming | N/A | 3
General Rooms/Spaces | Consult Room | Consult Room, Audiology Rehabilitation Counseling Room, Dental Consult Room |  | CONSULTATION | CPT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | 75 | 70 | 60 | - | 4 | 2 | Return | 40 | NR | -- | 6 |  |  |  | Multilevel Switching, Dimming & Occupancy | Multi-level switching or manual dimming | N/A | 1
General Rooms/Spaces | Procedure Room | Procedure Room, General, Urology, Gynecology, Specialty Care, Multi-Specialty Care, Cast Room | PROCEDURE | TREATMENT | WSF | WSF | EP | RWC | 4'-0" | SEE FGI | AT | 9'-0" | 3 | 3'-0" --------------- 3'-6" | Flush | Wood | -- | -- | 12 SE | 3 | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | 7 |  | P13 |  | Multilevel Switching, Dimming & Occupancy | Wall mounted exam light | N/A | 2
General Rooms/Spaces | Laboratory | Laboratory (Typical) | LABORATORY WORKROOM | __ | WSF | WSF | EP | -- | -- | 40 | AT-SP | 9'-0" | 3 | 3'-0" | Flush | Wood | _ | _ | 15 AG | 4 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 |  | P3, P4 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 5
General Rooms/Spaces | Conference Room | Conference Room, Multi-Purpose Room, Group Room, Shared Medical Appointment Room, Education Room, Staff Training Room, Classroom |  | __ | CPT | RB | P | RWC | 4'-0" | 40 | AT | 9'-0" | 17 | 3'-6" | Flush | Wood | _ | _ | 15 S | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | M2 | 8 |  | P14 |  | Multilevel Switching, Dimming & Occupancy | Provide 4 scene preset dimmable lighting for a variety of tasks. Consider placement and optics to mitigate glare and ceiling reflections. | N/A | 4
General Rooms/Spaces | TOILET | General Toilet, Patient - Toilet, Toilet - Police, Toilet - Family, Toilet - Female Staff, Toilet - Male Staff, Toilet - Procedure Room, Toilet - Public, Toilet - RF Patient, Toilet - Women's Health, Toilet - Female, Toilet - Family Assist, Specimen Collection Toilet | TOILET ROOM | TOILET ROOM | PT | PT | P | CT | 7'-0" | SEE FGI | AT | 9'-0" | 1,2 | 3'-6" | Flush | Wood | _ | _ | 11 | _ | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 |  |  | Downlights/Mirror or vanity | Occupancy Sensor | N/A | N/A
General Rooms/Spaces | OFFICE | Any Office | -- | CONSULTATION | CPT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 CS |  | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | 4 | 1 |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
General Rooms/Spaces | WAITING | Waiting - Family - PACT, Waiting - PACT 3, Waiting - General - 20 People, Waiting - General - 10 People, Waiting - General - 6 People, Waiting-General |  | EXAM - PUBLIC SPACE | CPT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 10, 17 | [7 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | M4 | -- | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
General Rooms/Spaces | RECEPTION | Reception, Information Desk, Travel Window, Reception - Accessible | -- | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" | -- | 3'-0" | Flush w/ narrow vision | Wood | _ | _ | 12 CG | 3 | _ | _ | _ | _ | _ | _ | _ | _ | _ | M4 | 1 | 1 |  | Downlights, pendants, decorative, and accent | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 10
General Rooms/Spaces | COPY ALCOVE | Copy Alcove, Copier - Workroom, Copy / Office Supply Room, Copy Room | -- | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" | 6 | _ | _ | _ | _ | _ | _ | 6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 3 |  |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 3
General Rooms/Spaces | CLEAN UTILITY | Clean Utility, Clean Supply, Clean Workroom, Clean Linen, Sterile Storage, CBOC Sterile Supply Storage Room, Clean Scope, Dental Clean Cart, Central Sterile | -- | -- | RFT | RB | P | RWC | 4'-0" | -- | AT | 9'-0" | -- | 3'-0" | Flush | Wood | -- | 45 MIN | 121 AG | _ | 66 | 75 | 55 | 30 | 4 | _ | _ | _ | (+) | _ | 1 |  |  |  | Occupancy Sensor | N/A | N/A
General Rooms/Spaces | SOILED UTILITY | Soiled Utility Room, Recycled Material, Soiled Holding, Soiled Linen, Soiled Workroom, Soiled Supply, Soiled Cart | SOILED HOLDING / SOILED WORK ROOM | -- | WSF | WSF | P | RWC | 4'-0" | -- | AT | 9'-0" | 3 | 3'-0" | Flush | Wood | -- | 45 MIN | 121 AG | _ | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 2 | -- |  |  | Occupancy Sensor | N/A | N/A | --
General Rooms/Spaces | STORAGE | Storage - Medical Equipment, Storage - Shared Medical Appointments, DME - Prosthetics Storage, Storage - Homeless, EMS Storage, Storage - Bistro/Coffee Bar, Storage - Patient Clothing and Luggage, Laundry / Storage, Tray Cart Storage Area, Buld Storage, General Storage, Secure Storage, | CLEAN WORKROOM/CLEAN SUPPLY |  | RFT | RB | P | -- | -- | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 35 AG |  | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | 1 per wall, not to exceed 12' spacing | -- |  | Surface or chain mounted 1' x 4' | Occupancy Sensor | N/A | N/A
General Rooms/Spaces | JANITOR'S CLOSET | Housekeeping Aides Closet (HAC) | ENVIRONMENTAL SERVICES ROOM | -- | CS | RB | P | FRP | 4'-0" | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 34 A | _ | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 | -- |  |  | Occupancy Sensor | N/A | N/A | --
General Rooms/Spaces | KITCHENETTE | Social Activities Space/ Kitchen | -- | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" | 17 | 3'-0" | Flush | Wood | -- | -- | 15 A | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | 4 | -- |  |  | Multilevel switching/dimming/occupancy | N/A | N/A | --
General Rooms/Spaces | EQUIPMENT ALCOVE | AED Alcove, Height and Weight Alcove, Scale Alcove, Stretcher Alcove, Med Alcove, Portable Patient Lift Alcove, Wheelchair Alcove, My Health eVet, Kiosk, | -- | -- | Match Adjacent | Match Adjacent | Match Adjacent | RWC | 4'-0" | -- | AT | Match Adjacent | 3 | -- | -- | -- | -- | -- |  | 6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
General Rooms/Spaces | STAFF LOUNGE | Staff Lounge | -- | -- | RSF | RB | P | -- | -- | 40 | AT | 9'-0" | 4 | 3'-0" | Flush w/ narrow vision | Wood | -- | -- | 13 | _ | _ | _ | _ | _ | _ | _ | Exh. (G) | _ | (-) | _ | 8 | -- | P7 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
General Rooms/Spaces | MEDICATION ROOM | Medication Room | MEDICATION ROOM | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 34 |  | -- | -- | -- | -- | -- | -- | -- | -- |  |  | 5 | 1 |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
General Rooms/Spaces | LACTATION ROOM | Employee Wellness, Lactation Room, Quiet Room | -- | -- | RFT | RB | P | -- | -- | 50 | AT | 9'-0" | 10 | 3'-0" | Flush | Wood | -- | -- | 12 CS |  | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
General Rooms/Spaces | LOCKER ROOM | Locker Room, Locker Room (Male/ Female) Locker - Staff Personal Property, Locker Room - Staff | -- | -- | RFT | RB | P | -- | -- | 40 | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | Push/Pull |  | -- | -- | -- | -- | -- | -- | Exh. (G) | -- | (-) | -- | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
General Rooms/Spaces | OFFICE, CUBICLE, Open Office | Cubicle - Administrative, Data Processing, Workstation - Extended Team, Homeless, Workstation - MICHM, Workstation - Suicide Prevention, Workstation - VOC Rehab, Workstation - Rad Tech, Workstation - Shipping / Receiving, Workstation, Administration (MSA MH; Rad, LPN), Workstation-Sleep Tech, Work Station, Call Center (MSA), Workstation-Cart Case Dispatch, Workstation-Clerical, | -- | -- | CPT | RB | P | -- | -- | -- | AT | 9'-0" | [8 empty] | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | 2 per workstation | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
General Rooms/Spaces | SUB-WAITING | Sub-Waiting, MRI Sub-Waiting, CT Sub-Waiting, Mammo Sub-Waiting, Sub-Waiting - Diagnostic Patient, Sub-Waiting - Dilation Patient, CT Vestibule, Waiting, Waiting-Zone 1, Sub-Waiting-Zone 2 | -- | -- | CPT | RB | P | -- | -- | -- | AT | 9'-0" | 2019-10-17 | -- | -- | -- | -- | -- | - | 6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | M4 | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
General Rooms/Spaces | VENDING | Vending Machine Area |  |  | RFT | RB | P | -- | -- | -- | AT | 9'-0" |  | -- | -- | -- | -- | -- | -- | 6 | _ | _ | _ | _ | _ | _ | _ | _ | _ | M4 | 8 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
General Rooms/Spaces | TOILET/SHOWER ROOM | Toilet/Shower-Staff, Toilet/Shower-Patient, Toilet/Shower-Female Staff, Toilet/Shower-Male Staff | TOILET ROOM | TOILET ROOM | PT | PT | CT | -- | -- | SEE FGI | GWB/P | 9'-0" | 2, 19 | 3'-6" | Flush | Wood | -- | -- | 11 G |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 2 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A
General Rooms/Spaces | CHANGING ROOM | Dressing room |  |  | RFT | RB | P | -- | -- | 40 | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 11 K |  | 75 | 70 | 60 | - | 4 | 2 | Return | NR | NR |  | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A
Primary Care, Specialty Care, PACT | PACT TEAM WORK SPACE | PACT Team Work Space, Team Work Area- Home Based Primary Care |  | -- | CPT | RB | P |  |  | -- | AT | 9'-0" | -- | _ | _ | _ | _ | _ | 14 MP | 6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | M3 | 2 per workstation | -- |  |  | Multilevel Switching, Dimming & Occupancy | Provide dimming and switching to provide various light levels. Provide switching in refraction desk to control overhead lighting. | N/A | 1 per workstation
Primary Care, Specialty Care, PACT | EXAM ROOM, AIRBORNE INFECTION ISOLATION | Exam, Isolation, Negative Pressure | AII Room | EXAMINATION | WSF | WSF | P | -- | -- | SEE FGI | GWB:P | 9'-0" | 3,7 | 3'-6" | Flush | Wood | -- | -- | 12 S |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | -- | -- | -- | Multilevel Switching, Dimming & Occupancy | Sealed fixture, flat lens surface on exterior | N/A | 1
Audiology and SLP | AUDIOLOGY HEARING AID TESTING | Hearing Aid Lab, Hearing Aid Processing, Hearing Aid Repair |  | -- | RFT | RB | P | -- | -- | 40 | AT | 9'-0" | -- | 3'-0" | Flush | Wood | _ | _ | 15 S | _ | 75 | 70 | 60 | - |  |  | Exh. (G) |  | (-) |  | 7 | 0 | P4 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
Audiology and SLP | AUDIOLOGY HEARING AID FITTING | Audiology Programming / Fitting, Hearing Aid Fitting Room, Cerumen Management Room, Speech Language Pathology Assistive Technology Room, Speech Language Pathology Voice Treatment Room | EXAM | -- | CPT | RB | P | -- | -- | 60 | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | -- | 12 S | _ | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | -- | -- | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
Audiology and SLP | AUDIOMETRIC EXAM BOOTH | Audiometric Exam Suite, Exam - Audiometric Booth, Aud: Suite - Audiometric Exam, Hearing/Diagnostics, Booth, 1-Person | EXAM | -- | Pre-Fab | Pre-Fab | Pre-Fab | -- | -- | SEE EQUIP LIST | Pre-Fab | 8'-0" | -- | 3'-0" --------------- 3'-6" | Pre-Fab | Pre-Fab | _ | _ | 1 | 2,4 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 9 | -- | P1 | -- | Typically pre-packaged unit including lighting and switching | N/A | L1 | 5
Audiology and SLP | ELECTROPHYSIOLOGY | Electrophysiology, Posturography, Vestibulography | EXAM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 |  | P2, P3, P14 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 3
Dental Service | SPECIALTY EQUIPMENT MECHANICAL ROOM | Dental Equipment Mech. Room, Mechanical Rooms - Electrical | -- | -- | CS | -- | P | -- | -- | 60 | EXP | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 14 S | [7 empty] | Exh. (G) |  | (-) |  | 2 | -- | P3 | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | 1
Dental Service | DENTAL PROSTHETICS LABORATORY | Laboratory, Dental Prosthetics | -- | -- | WSF | WSF | P | -- | -- | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 15 AG |  | 75 | 70 | 60 | 20 | 6 | 2 | Return Exh. (G) | 45 | (-) | M13 | 7 | -- | -- | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 5
Dental Service | DENTAL TREATMENT ROOM | Dental Treatment Room (DTR), Multi-Functional (4/Hygiene), Special Needs Patient, Bariatric | EXAM | TREATMENT | WSF | WSF | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 CS | [9 empty] | (+) |  | 7 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Dental Service | DENTAL X-RAY ROOM | X-Ray Room, Panoramic / Cephalometric (Cone Beam) | CLASS 1 IMAGING ROOM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 5 | 3'-6" | Flush | Wood | -- | LEAD LINED | 17 AGL | 8 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 7 | -- | P3 | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Optometry | FITTING & DISPENSING, EYEGLASSES | Fitting & Dispensing, Eyeglasses |  | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | 6 | 75 | 70 | 60 | - | 4 | 2 | Return | 40 | NR |  | 2 |  |  | Downlights and accent/display | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
Optometry | LOW VISION EXAM/ THERAPY/ TRAINING | Low Vision Exam/ Therapy/ Training | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | -- | -- | -- | Multilevel Switching, Dimming & Occupancy | Provide dimming and switching to provide various light levels. Provide switching in refraction desk to control overhead lighting. | N/A | 3
Optometry | PRE-TESTING/ INTAKE | Pre-Testing/ Intake | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | [10 empty] | 6 | 1 |  |  | Multilevel Switching, Dimming & Occupancy | Provide dimming and switching to provide various light levels. Provide switching in refraction desk to control overhead lighting. | N/A | 2
Optometry | VISUAL FIELDS ROOM | Visual Fields Room, Photography Room, Ultrasound Room, Tomography Room, Imaging Room, OCT Laser | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 7 | -- | -- | -- | Multilevel Switching, Dimming & Occupancy | Provide dimming and switching to provide various light levels. Provide switching in refraction desk to control overhead lighting. | N/A | 2
Mental Health | QUIET ROOM | Quiet Room for Patients | EXAM | TREATMENT | CPT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 35 S | [11 empty] | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Mental Health | BIOFEEDBACK TREATMENT ROOM | Biofeedback Treatment Room | EXAM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 15 S |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4 | -- |  | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
Specialty Care Services | PULMONARY FUNCTION ROOM | Pulmonary Function - Analysis | EXAM | TREATMENT | WSF | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 G | [11 empty] | 6 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
Specialty Care Services | TREADMILL ROOM | Treadmill Room | EXAM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 MS |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | -- | P9 | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
Specialty Care Services | EKG TESTING ROOM | EKG Testing Room | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0 |  | 3'-6" | Flush | Wood | -- | -- | 12 S | [11 empty] | One per wall | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
Recreation Therapy | GROUP THERAPY ROOM, MUSIC | Creative Arts - Group Therapy Room - Music | -- | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 CG |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 8 | -- |  | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Recreation Therapy | GROUP THERAPY ROOM, ART | Creative Arts - Group Therapy Room - Large | -- | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 CG | [11 empty] | 8 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Recreation Therapy | WEIGHT ROOM, SMALL | Recreation Therapy Exercise / Weight Room - Small | -- | TREATMENT | RF | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 34 AG |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 12 | -- |  | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
PHYSICAL THERAPY | PHYSICAL THERAPY GYM | Treatment Exercise Area (includes workstations therapists) | EXAM | TREATMENT | RF | RB | P | -- | -- | SEE FGI | AT | 10'0" |  | 3'-6" | Flush | Wood | -- | -- | 14 S | [11 empty] | 14 | -- | P14 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
PHYSICAL THERAPY | Activities Daily Living (ADL) Training | ADL Evaluation and Training Center, Toilet, Tub, Bed, Kitchen, Laundry | EXAM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0 |  | 3'-6" | Flush | Wood | -- | -- | 15 S |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4 | -- |  | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A
Imaging Services | RADIOLOGY | Radiology, ES: General Purpose Radiology Room | CLASS 1 IMAGING ROOM | TREATMENT | WSF | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 5 | 4'-0" | Flush | Wood | -- | LEAD LINED | 15 LS | 8 | [10 empty] | 5 |  | P3, P13 |  | Fully dimmable, occupancy sensor | N/A | L2 | 2
Imaging Services | C.T. CONTROL ROOM | CT Control Area, X-Ray - Computed Tomography - Control | -- | TREATMENT | WSF | WSF | P | -- | -- | SEE FGI | AT | 9'-0" | 5 | 3'-0" | Flush | Wood | -- | LEAD LINED | 12 LS |  | -- | -- | -- | -- | -- | -- | -- | 45 | -- | M14 | 6 | -- | P3 | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
Imaging Services | C.T. EQUIPMENT ROOM | CT Equipment Room, X-Ray - Computed Tomography - Indep View Console |  | -- | WSF | WSF | P | -- | -- | -- | AT | 9'-0" | 5 | 6'-0" | Flush | Wood | -- | -- | 45 AG | 7 | [7 empty] | 50 |  | M14 | 7 | -- | P3, P13 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
Imaging Services | C.T. SCAN ROOM | CT Scanning Room (Ceiling Lift), X-Ray - Computed Tomography - Scanner | CLASS 1 IMAGING ROOM | TREATMENT | WSF | WSF | P | -- | -- | SEE FGI | AT | 9'-0" | 5 | 4'-0" | Flush | Wood | -- | LEAD LINED | 15 ALG |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 7 | -- | P3, P13 | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Imaging Services | MAMMOGRAPHY SCAN ROOM | Mammo - X-ray, Mammography Room | CLASS 1 IMAGING ROOM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 5 | 3'-6" | Flush | Wood | -- | LEAD LINED | 12 LS | [11 empty] | 7 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Imaging Services | RADIOGRAPHIC / FLOURO SCAN ROOM | Radiographic / Fluoroscopic (R/F) Room | CLASS 1 IMAGING ROOM | TREATMENT | WSF | WSF | P | - | - | SEE FGI | AT | 9'-0" | 5 | 3'-6" | Flush | Wood | -- | LEAD LINED | 15 AGL |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 7 | -- | P3, P13 | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Imaging Services | ULTRASOUND SCAN ROOM | Ultrasound Room | CLASS 1 IMAGING ROOM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 S | [11 empty] | 7 | -- | P3, P13 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Imaging Services | PACS SERVER ROOM | X-Ray - Storage - Digital Files, Viewing Room - Picture Archiving and Communication System (PACS) | -- | -- | RFT | RB | P | - | - | - | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 15 GK |  | -- | -- | -- | -- | -- | -- | -- | 50 | -- | -- | 4 | -- | P3, P13 | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
Imaging Services | MRI CONTROL ROOM | MRI Control Room, X-Ray - Magnetic Resonance - Control, MRI Zone 3 | CLASS 1 IMAGING ROOM | EXAM - MRI | RFT | RB | P | -- | -- | 40 | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 12 GS | [8 empty] | 45 |  | M14 | 6 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
Imaging Services | MRI EQUIPMENT ROOM | MRI System Component Room, X-Ray - Magnetic Resonance - System Component | -- | TREATMENT | RFT | RB | P | RWC | 4'-0" |  | AT | 9'-0" | 11 | 4'-0" | Flush | Wood | -- | -- | 35 AG |  | -- | -- | -- | 40 | -- | -- | -- | 50 | -- | M14 | 7 | -- | P3 | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Imaging Services | MRI FERROMAGNETIC DETECTION | X-Ray - Magnetic Resonance - Ferromagnetic Detection, MRI Zone 2, MRI Viewing Room |  | EXAM - MRI | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 2019-11-16 | 4'-0" | Flush | Wood | -- | -- | 15 G |  | 75 | 70 | 60 | 40 | 12 | 2 | Return | 40 | NR |  | 1 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
Imaging Services | MRI SCAN ROOM | MRI Scanning, X-Ray - Magnetic Resonance - Scanner, | -- | EXAM - MRI | WSF | RB | P | -- | -- | SEE FGI | AT | VARIES | 11,13,16 | 4'-0" | Flush | Wood | -- | R/F Shielded | 1 | -- | 75 | 70 | 60 | 40 | 12 | 2 | Return Exh. (S) | 50 | NR | M17 | 2 | -- | P3 | -- | Multilevel Switching, Dimming & Occupancy | MRI rated fixtures | N/A | 1
Imaging Services | READING ROOM | MRI Viewing Room, X-Ray - Magnetic Resonance - Viewing |  | -- | CPT | RB | P | -- | -- | 40 | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 12 GS | [8 empty] | 40 |  |  | 6 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 6
Imaging Services | BONE DENSITOMETRY | Bone Densitometer | EXAM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 35 S |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 7 | -- | P3 | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
Pathology and Laboratory Medicine | SPECIMEN COLLECTION | Blood Specimen Collection, Alcove - Specimen Collection Point of Care (also for Substance Abuse plus Coumadin), Blood Draw Alcove, Support Area, Laboratory-Satellite, Laboratory-Venipuncture, Blood Draw | EXAM | __ | WSF | WSF | EP | -- | -- | -- | AT | 9'-0" | 3 | -- | _ | _ | _ | _ | _ | 6 | [10 empty] | 4 |  |  |  | Multilevel Switching, Dimming & Occupancy | Multi-level switching or manual dimming | N/A | 2
Pathology and Laboratory Medicine | SPECIMEN ACCESSIONING, PROCESSING & DISTRIBUTION ROOM | Specimen Accessioning, Processing & Distribution Room | LABORATORY WORK ROOM | -- | WSF | WSF | EP | -- | -- | -- | GYP/EP or AT-SP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 15 AG |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | One per wall, 6' spacing, one adjacent to sink | One at each workstation |  |  | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | One at each workstation
Pharmacy Service | PHARMACY | Pharmacy, Pharmacy, PACT 3 (Controlled Substance) (w/3 AutoDispensing) | PHARMACY | -- | RF | RB | P | -- | -- | -- | AT | 9'-0" | -- | 6'-0" | Flush | Metal | - | - | 200 AS | 7 | [10 empty] | 15 |  | P5 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 9
Pharmacy Service | PHARMACY DISPENSING WINDOW | Dispense/Consult Window, Workroom, Pharmacist | PHARMACY | -- | RF | RB | P | -- | -- | -- | AT | 9'-0" | -- | - | - | - | - | - | - | OPEN | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 12 |  |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 5
Pharmacy Service | CLEAN ROOM, COMPOUNDING | Pharmacy - Clean Room - Chemotherapy Compounding | -- | -- | RF | RF | P | -- | -- | -- | GWB:P | 9'-0" | 3 | 7'-0" | Single Slide Auto Sliding Door | Aluminum/ Glass | Yes | -- | 850 |  | 68 | 68 | 60 | 20 | 30 | 2 | Exh. (S) | 55 | (-) | M12 | 14 | -- | P10 |  | Multilevel Switching, Dimming & Occupancy | Sealed fixture, flat lens surface on exterior | N/A | 5
Pharmacy Service | IV ADMIXTURE | Pharmacy - IV Admixture - Low Volume | -- | -- | RF | RF | P | -- | -- | -- | GWB:P | 9'-0" | 3 | 7'-0" | Single Slide Auto Sliding Door | Aluminum/ Glass | Yes | -- | 850 |  | 68 | 68 | 60 | 20 | 30 | 2 | Return | 55 | (++) | M12 | 14 | -- | P10 |  | Multilevel Switching, Dimming & Occupancy | Sealed fixture, flat lens surface on exterior | N/A | 5
Pharmacy Service | PRESCRIPTION DISPENSING AREA | Prescription Dispensing Area - OmniCell Station | -- | -- | RF | RF | P | -- | -- | -- | AT | 9'-0" | 3 | -- | -- | -- | -- | -- | - | 6 | [10 empty] | 8 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
Pharmacy Service | SECURE STORAGE VAULT | Secure Storage, Vault | CLEAN WORK ROOM/ CLEAN SUPPLY | -- | RFT | RB | P | RWC | 4'-0" | -- | GWB:P | 9'-0" | -- | 3'-0" | Flush | Hollow Metal | -- | -- | 1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 | -- | -- | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
Pharmacy Service | ANTEROOM | Anteroom, Compound Sterile Preparation |  | -- | WSF | WSF | EP | -- | -- | -- | GWB:SP | 9'-0" | 3 | 7'-0" | Single Slide Auto Sliding Door | Aluminum/ Glass | Yes | -- | 850 |  | 68 | 68 | 60 | 20 | 30 | 2 | Return | 55 | (+) | M12 | 2 | -- |  |  | Multilevel Switching, Dimming & Occupancy | Sealed fixture, flat lens surface on exterior | N/A | --
Business Office | SECURE CASH ROOM | Secure Money Handling Room | -- | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0 | -- | 3'-0" | Flush w/ 1-Way Viewer | Steel | -- | -- | 200 GV | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4 | -- |  |  | Multilevel switching/dimming/occupancy | N/A | N/A | 1
Engineering | BIOMED. REPAIR SHOP | Repair Shop, Biomedical Eng. | -- | -- | RF | RB | P | -- | -- | -- | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 35 AG | [7 empty] | Exh. (G) |  | (-) | M7 | 10 | -- | P4, P6 | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | 2
Logistics | LOADING DOCK | Receiving/ Shipping Dock | -- | -- | CS | RB | EP | -- | -- | -- | EXP. | -- | 8 | 6'-0" | Flush | Wood | -- | -- | 44 APW | 7 | - | 60 | - | - |  |  | Exh. (G) |  | (+) | M5 | 2 | -- |  | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | 2
Logistics | MAIL ROOM | Support: Mail Room and Dist. Center, Mailing Room - Prosthetic Appliances | -- | -- | RF | RB | P | RWC | 4'-0" | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 15 G | [11 empty] | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
Logistics | GAS CYLINDER STORAGE | Storage - Gas Cylinders - MRI, Storage - Gas Cylinders - Interior | -- | -- | WSF | RB | P | RWC | 4'-0" | -- | AT | 9'-0" | -- | 3'-0" | Flush | Wood | -- | 45 MIN | 34 G | -- | -- | -- | -- | -- | -- | -- | Exh. (S) | -- | (-) | -- | 1 | -- | -- | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
Logistics | BIO-HAZARD STORAGE | Storage - Bio Hazardous Material, Storage - Hazardous Material, Infectious / Hazardous Waste | REGULATED WASTE | -- | WSF | WSF | EP | RWC | 4'-0" | -- | GWB:SP | 9'-0" | 3 | 3'-6" | Flush | Hollow Metal | -- | -- | 34 G | [11 empty] | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
Logistics | STORAGE WAREHOUSE | Bulk Storage, General Storage, Warehouse | CLEAN WORKROOM/CLEAN SUPPLY | -- | CS | RB | P | -- | -- | -- | Exp | 10'-0" | -- | 6'-0" | Flush | Wood | -- | -- | 45 AG | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | minimum, 1 per wall, not to exceed 12' spacing | -- | -- | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A
Logistics | BREAK DOWN | Break Down | CLEAN WORKROOM/CLEAN SUPPLY |  | RPT | RB | EP | -- | -- | -- | AT | 9'-0" | 8 | 4'-0" | Flush | Wood | -- | -- | 34 AG | [11 empty] | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A
Police Service | POLICE HOLDING ROOM | Holding Room | -- | -- | CS | RB | P | -- | -- | -- | GWB-PT | 9'-0" | 3,15 | 3'-6" | Flush | Hollow Metal | Half Glass w/ Laminated Glass |  | 18 P | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | Multilevel Switching, Dimming & Occupancy | Tamperproof fixture design | N/A | --
Police Service | OPERATIONS ROOM | Operations Room |  |  | RFT | RB | P | -- | -- | 40 | AT | 9'-0" |  | 3'-6" | Flush | Hollow Metal | -- | -- | 200 APS | [10 empty] | M15 | 0 | 8 |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
Police Service | SECURE STORAGE | Small Arms Armory, Storage - Secure | -- | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" | -- | 3'-0" | Flush | Hollow Metal | -- | -- | 200 P | -- | 75 | 70 | 60 | - | 4 | 2 | Return | NR | NR |  | 1 | -- | -- | -- | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
VCS | RETAIL AREA | Retail Area |  | EXAM - PUBLIC SPACE | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0 | 17 | 6'-0" | Flush w/ Full Vision | Wood | Full Vision |  | 47 KM | 7, 9 | [9 empty] | M4 | One per wall, 6' spacing | -- |  |  | Multilevel Switching, Dimming & Occupancy | Track or adjustable accent lighting for retail displays. | L5 | 3
OI&T | TELECOMM. | Telecommunications Room/ Closet, IT Telecommunications Room | -- | -- | RFT | RB | P | -- | -- | -- | EXP. | 12'-0" | -- | 3'-6" | Flush | Wood | -- | -- | 34 AS | -- | 75 | 64 | 55 | 30 | - | - | - | - | NR |  | 6 | -- | P15 | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | --
OI&T | SERVER ROOM | Central Server Room | -- | -- | RFT | RB | P | -- | -- | -- | EXP. | 12'-0" |  | 3'-6" | Flush | Wood | -- | -- | 34 AS |  | 81 | 72 | 60 | 6 | [5 empty] | M8 | 10 | -- | P15 | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | --
OI&T | I.T. WORKROOM | IT Workroom, Equip. Configuration/ Repair | -- | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" | -- | 3'-0" | Flush | Wood | -- | -- | 35 AG | -- | [10 empty] | 10 | -- | P4, P6 | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | 8
SPS | ANTEROOM, SOILED TRANSITION | Anteroom, Soiled Transition/Drop-Off | DECONTAM ROOM | -- | RES | RES | EP | -- | -- | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 66 | 72 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (-) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 2
SPS | DECONTAMINATION ROOM | Decontamination Work Room, Scope Decontamination Room | DECONTAM ROOM | -- | RES | RES | EP | -- | -- | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG | -- | 66 | 72 | 60 | 30 | 6 | 6 | Exhaust (G) | 40 | (--) | -- | One per wall | -- | -- | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 4
SPS | Cart Wash | Cart Wash |  | -- | RES | RES | CT |  |  | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 70 | 75 |  |  | 10 | 10 | Exhaust (S) | 40 | (-) | M18, M19 | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A
SPS | Water Treatment Storage Room | Water Treatment Storage Room | -- | -- | RES | RES | EP | -- | -- | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush | Steel |  | -- | 15 AG | -- | 70 | 75 |  |  | 10 | 10 | Exhaust (G) | 40 | (-) | M18, M19 | One per wall | -- | -- | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 1
SPS | REPROCESSING ROOM, SCOPE | Reprocessing Room, Scope |  | -- | RES | RES | EP |  |  | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 66 | 72 | 60 | 30 | 6 | 6 | Exhaust (G) | 40 | (-) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 2
SPS | Instrument Assembly | Instrument Assembly | -- | -- | WSF | WSF | EP | -- | -- | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG | -- | 66 | 72 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (++) | -- | One per wall | -- | -- | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 4
SPS | Sterilization Area | Steam Sterilization Area, Low Temp Sterilization Area |  | -- | RES | RES | EP |  |  | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 66 | 75 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (++) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 2
SPS | Cooling Area | Cooling Area | -- | -- | RES | RES | EP | -- | -- | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG | -- | 66 | 75 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (++) | -- | One per wall | -- | -- | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 1
SPS | Equipment Room, Steam Generator | Equipment Room, Steam Generator |  | -- | RFT | RB | EP |  |  | -- | ACT-SP | 9'-0 | 3, 7 | 3'-6" | Flush | Steel |  | -- | 15 AG |  | 85 |  |  |  | 10 | 10 | Exhaust (G) | 45 | (-) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | --
SPS | Clean Dispatch | Clean Dispatch | -- | -- | RFT | RB | EP | -- | -- | -- | ACT-SP | 9'-0 | 3, 7 | -- | -- | -- | -- | -- | -- | -- | 70 | 75 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 |  | -- | One per wall | -- | -- | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 1
SPS | STORAGE, CLEAN SCOPE | Storage, Clean Scope | CLEAN SUPPLY | -- | RES | RES | EP | RWC | 4'-0" | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 15 AG |  | 66 | 75 | 55 | 30 | 4 |  |  |  | (+) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | --
CLC/Small House (House) | RESIDENT BATHROOM | Patient Toilet/Shower - Residential; Toilet | Toilet/Bathing Room | Resident Room/Dwelling Unit | PT/CT or poured epoxy | PT / CT or integral epoxy | GWB P/ CT | PT / CT | -- | STC 45 | GWB P | 9'-0 | Grab bars need to be provided at the toilet | 3'-6" | Barn/Sliding | Wood - no Lite | -- | -- | 11 | Sliding Pull | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 | -- | -- | F1, F2, F3 | Occupancy | N/A | Coordinate lighting with plumbing fixtures, vanities & wall-mounted equipment | 0
CLC/Small House (House) | RESIDENT BEDROOM | Patient Room Residential; Transitional Rehab Resident Bedroom | Resident Room | Resident Room/Dwelling Unit | RFT | PRB / RB | GWB P | -- | -- | STC 45 | GWB P | 9'-0 | -- | 4'-0" | Flush | Wood - no Lite | -- | -- | 17S | -- | 75 | 70 | 60 | 30 | 4 | 2 | Return | 35 | (o) | -- | 6 | -- | -- | F4, F5, F6 | Multilevel Switching (CFL), Dimming (LED) | N/A | N/A | 2
CLC/Small House (House) | LIVING ROOM | Day Room | Resident Living | Community Space | CPT/ LRT/ RSF | PRB / RB | GWB P / Wood / Tile / Stone | -- | -- | -- | GWB P | 10'-0 | -- | -- | -- | -- | -- | -- | -- | -- | 75 | 70 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Provide a project-specific unoccupied mode for unoccupied hours | 4 (incl. 2 floor mount) | -- | -- | F7, F4, F5, F8, F6 | Multilevel Switching (CFL), Dimming (LED) | N/A | N/A | 0
CLC/Small House (House) | DINING ROOM | Canteen | Resident Dining | Community Space | PT/ LRT/ PT/ CT/ Wood/ RSF | PT / PRB / Wood | GWB P / Wood | -- | -- | -- | GWB P | 10'-0 | -- | 3'-6" (if any) | Flush (if any) | Wood (if any) | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 2 (incl. 2 floor mount) | -- | -- | F7, F4, F8, F9, F10 | Multilevel Switching (CFL), Dimming (LED) | Local controls accessible by staff only. Lamps must be fully-enclosed by luminaire | N/A | 1
CLC/Small House (House) | KITCHEN | Canteen; Kitchen & Servery | -- | Community Space | PT/ LRT/ ET/ Tile or Wood | PT/ PRB | GWB P | -- | -- | -- | GWB P | 10'-0 | -- | None (open room) | None (open room) | -- | -- | -- | -- | -- | 75 | 70 | 60 | -- | 6 | 2 | Exhaust (G) & (S) | 40 | (-) | Kitchen Hood Exhaust, comply with applicable version of NFPA 101 | 14 | -- | One dedicated receptacle per stove and one per oven | F7, F4, F8, F9, F10 | Multilevel Switching (CFL), Dimming (LED) | Lamps must be fully-enclosed by luminaire | N/A | 1
CLC/Small House (House) | DEN | Office | -- | Community Space | CPT/ LRT / Carpet | PCT/ PRB | GWB P | -- | -- | STC 45 | GWB P | 9'-0 | -- | 3'-6" | French with blinds & side lite | Steel w/ lite | -- | -- | 12S | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 5 | -- | -- | F7, F11, F12, F13 | Multilevel Switching (CFL), Dimming (LED) | N/A | N/A | 1
CLC/Small House (House) | LAUNDRY | Laundry Room; Residential Rehab Treatment Program - Living Area, Dining Area, Kitchenette | Laundry | -- | RT/ RSF | RB/ PRB | GWB P | -- | -- | STC 45 | ACT | 9'-0 | -- | 4'-0" | Flush | Wood - no Lite | -- | -- | 12KS | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | -- | One dedicated outlet per dryer | F1, F13 | Multilevel Switching (CFL), Dimming (LED) | N/A | N/A | 0
CLC/Small House (House) | BATHING ROOM | Bathing Suite; Patient Toilet/Shower | -- | Toilet Room | CT/ PT | CT/ PT | GWB P/ CT | CT / PT | -- | STC 45 | GWB P | 9'-0 | Grab bars need to be provided at the toilet | 3'-6" (toilet) 4'-0 (shower) | Flush | Wood - no Lite | -- | -- | 11 | -- | 75 | 82 | 60 | -- | 10 | 2 | Exhaust (S) | 40 | (-) | -- | 5 | -- | -- | F1, F2, F3 | Multilevel Switching (CFL), Dimming (LED) | N/A | N/A | 0
CLC/Small House (House) | FOYER |  | -- | Corridor (with entrance) | PT/ LRT | PT/ PRB | GWB P | -- | -- | -- | GWB P | 9'-0 | -- | -- | -- | -- |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 2 min. | -- | -- | -- | Multilevel Switching (FL), Dimming (LED) | N/A | N/A | --
CLC/Small House (House) | CORRIDOR / SITTING ALCOVE | Primary Corridor | -- | Corridor | CPT/ LRT | PRB | GWB P | -- | -- | -- | GWB P | 9'-0 | -- | -- | None (open room) | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Per NEC | -- | -- | F7, F4, F8, F5 | Multilevel Switching (CFL), Dimming (LED) | N/A | Refer to NFPA 101 for egress lighting requirements | 1
CLC/Small House (House) | PANTRY | Canteen | Dietary Storage | -- | PT/ LRT/ ET | PT/ PRB | GWB P | -- | -- | -- | ACT | 9'-0 | -- | 3' 0" | Flush | Wood | -- | -- | 14 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4 | -- | -- | 2 X 4 recessed lensed, efficient lighting | Multilevel Switching (CFL), Dimming (LED) | N/A | N/A | --
CLC/Small House (House) | GARAGE / RECEIVING | Maintenance Garage; Loading Dock | -- | -- | RT/ RSF/ EP | RB/ EP | GWB P | -- | -- | -- | GWB P | 10'-0 | -- | 3'-6 (passage) 10'-0 (roll up) | Flush | Steel | -- | -- | 14 | -- | -- | 60 | 60 | 15 | -- | 100% | Exhaust (S) | 50 | (-) | Ref. VA HVAC Design Guide | One per wall | -- | -- | F14, F15, F19 | Multilevel Switching (FL), Dimming (LED) & Occupancy | N/A | If industrial lights, provide lap shield or guard. | --
CLC/Small House (House) | HOUSE STAFF OFFICE | Offices; Administrative Office; Home Office | -- | -- | CPT | PRB/ RB | GWB P | -- | -- | STC 35 | ACT | 9'-0 | -- | 3'-6" | French with blinds & side lite | Wood | Narrow Vision | -- | 12S | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | -- | -- | F14, F11, F12, F13, 2 x 2 CLF | Multilevel Switching (FL), Dimming (LED) | N/A | Under-cabinet task lights and desk lights shall be controlled with integrated switches. | 4
CLC/Small House (Neighborhood) | NEIGHBORHOOD CENTER LOBBY | Main Entrance Lobby; Main Lobby | Resident Living | Community Space | PT/ LRT | PT/ PRB | GWB P | -- | -- | -- | GWB P | 9'-0 min. | -- | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | One per wall min. | -- | -- | F4, F7, F8, F9 | Multilevel Switching (FL), Dimming (LED) | N/A | Wall-mounted sconces must be ADA compliant. Consider luminaire maintenance requirements when locating luminaires in high ceilings. Local controls shall only be accessible to staff. | 1 per workstation plus 1 for lobby
CLC/Small House (Neighborhood) | MULTIPURPOSE ACTIVITY ROOM | Multipurpose Room | Resident Activity | Community Space | CPT/ LRT | PRB | GWB P | -- | -- | STC 45 | ACT-SP | 10'-0 | -- | 4'-0" w/ 2'-0 leaf | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 13 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 10 | -- | -- | F7, F4, F8 | Multilevel Switching (FL), Dimming (LED) | N/A |  | 6
CLC/Small House (Neighborhood) | MULTIPURPOSE ACTIVITY STORAGE | Multipurpose Storage; Storage | -- | -- | RT | PRB | GWB P | -- | -- | STC 30 | ACT-SP | 8'-0 | -- | 3'-6" | Flush | Wood | -- | -- | 14 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 | -- | -- | F14, F15, F16 | Multilevel Switching (FL), Dimming (LED) | N/A | If industrial fixtures, provide with lamp shield or guard | --
CLC/Small House (Neighborhood) | CONFERENCE ROOM | -- | -- | -- | CPT | PRB | GWB P | -- | -- | -- | GWB P | 9'-0 min. | -- | 3'-6" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 13 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | One per wall min. | -- | -- | F7, F4, F17, F18 | Multilevel Switching (FL), Dimming (LED) | N/A | Consider luminaire placement and optics to mitigate glare and veiling reflections especially at presentation screen. | 2
CLC/Small House (Community Center) | COMMUNITY CENTER LOBBY | Main Entrance Lobby; Main Lobby | Resident Living | Community Space | PT/ LRT | PT/ PRB | GWB P | -- | -- | -- | GWB P | 9'-0 min. | -- | 4'-0" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | One per wall min. | -- | -- | F4, F7, F8, F9 | Multilevel Switching (FL), Dimming (LED) | N/A | Wall-mounted sconces must be ADA compliant. Consider luminaire maintenance requirements when locating luminaires in high ceilings. Local controls shall only be accessible to staff. | 1 per workstation plus 1 for lobby
CLC/Small House (Community Center) | CONCIERGE STATION | -- | -- | -- | CPT | PRB | GWB P | -- | -- | STC 35 | GWB P | 9'-0 | -- | None (open room) | None (open room) | Wood (if any) | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 9 | -- | -- | F4, F7, F8, F9 | Multilevel Switching (FL), Dimming (LED) | N/A | Wall-mounted sconces must be ADA compliant. Consider luminaire maintenance requirements when locating luminaires in high ceilings. Local controls shall only be accessible to staff. | 3
CLC/Small House (Community Center) | GREAT ROOM | Multi-Purpose Activity Room | Resident Activity | Community Space | CPT | PRB/ RB | GWB P | -- | -- | STC 35 | GWB P | 12'-0 (or taller) | -- | 3'-6" double doors (if any) or cased openings | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 13 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 11 | -- | -- | F7, F4, F8 | Multilevel Switching (FL), Dimming (LED) & Occupancy | N/A | N/A | 1
CLC/Small House (Community Center) | RETAIL STORE | Gift Shop (Retail Store); Veterans Canteen Service and Gift Store | Resident Activity | Community Space | LRT/ CPT | PRB | GWB P | -- | -- | STC 35 | ACT | 9'-0 | -- | 3'-6" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 13 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | As needed per retail layout; minimum one per wall | -- | -- | F7, F4, F8, F20 | Multilevel Switching (FL), Dimming (LED) | N/A | Coordinate general and accent lights with merchandise displays Local controls shall only be accessible to staff. | As needed per retail layout; minimum 1 per cash register
CLC/Small House (Community Center) | POST OFFICE | Mailroom, Lgstcs Scv; Mail Rooms; | Resident Activity | Community Space | RT/ CPT | PRB | GWB P | -- | -- | STC 35 | ACT | 9'-0 | -- | 4'-0" | Flush | Wood | -- | -- | 13 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | One per wall plus min. one per work station (if any) | -- | -- | F14, F15, F19 | Multilevel Switching (FL), Dimming (LED) | N/A | If using industrial fixtures, provide lamp with shield or guard. Coordinate luminaire placement with overhead cabinets & shelving. Do not install luminaire directly above. Coordinate luminaire placement with equipment. | 1 per workstation min.
CLC/Small House (Community Center) | THEATER | Auditoriums & Theaters | Resident Activity | Community Space | CPT/ LRT | PRB | GWB P | -- | -- | STC 45 | ACT | 10'-0 | -- | 4'-0" | Flush | Wood | -- | -- | 13S | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4 | -- | -- | See Lighting Notes | See Lighting Notes | N/A | No guideline reference. Use Illumination levels as a guide. A/E shall follow the most appropriate lighting guidance based on area/ room function, latest code requirements, industry and professional design practices. Vary illumination levels by dimming control devices in accordance with specific project requirements. | 1
CLC/Small House (Community Center) | LIBRARY | -- | Resident Activity | Community Space | CPT | PRB | GWB P | -- | -- | STC 30 | ACT | 10'-0 | -- | 4'-0" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 13S | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4 | -- | -- | See Lighting Notes | See Lighting Notes | N/A | No guideline reference. Use Illumination levels as a guide. A/E shall follow the most appropriate lighting guidance based on area/ room function, latest code requirements, industry and professional design practices. Vary illumination levels by dimming control devices in accordance with specific project requirements. | 3
CLC/Small House (Community Center) | HAIR CARE SALON | Hair Care (Barber/Beauty Salon); Barber Shop | Hair Salon | Community Space | LRT/ RSF | PRB | GWB P | -- | -- | STC 35 | ACT | 10'-0 | -- | 4'-0" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 13 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | At least 1 per work station (min 1 per wall) | -- | -- | F7, F1, F2 | Multilevel Switching (FL), Dimming (LED) | N/A | Coordinate luminaires with equipment and vanities. | 1
CLC/Small House (Community Center) | MEDITATION CHAPEL | Chapel/Meditation/Quiet Room; Chapel | Resident Activity | Community Space | CPT | PRB | GWB P | -- | -- | STC 45 | GWB P | 10'-0 | -- | 3'-6" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 13S | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | One per wall | -- | -- | See Lighting Notes | See Lighting Notes | N/A | No guideline reference. Use Illumination levels as a guide. A/E shall follow the most appropriate lighting guidance based on area/ room function, latest code requirements, industry and professional design practices. Vary illumination levels by dimming control devices in accordance with specific project requirements. | --
CLC/Small House (Community Center) | PT / OT EXERCISE GYM | Rehabitation Therapy Gym; Physical/Occupational Therapy | Physical Therapy | -- | RBS | RB | GWB P | -- | -- | -- | ACT | 10'-0 | -- | 3'-6 double doors | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 13 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | -- | -- | F7, F4, F8, F17, F13 | Multilevel Switching (FL), Dimming (LED) | N/A | Under-cabinet task lights shall be controlled with integrated switches. | 1
CLC/Small House (Community Center) | TEAM WORKROOM | Multi-purpose Room; Team/Break Room | -- | -- | CPT | PRB/ RB | GWB P | -- | -- | -- | ACT | 9'-0 | -- | 3'-6" | Flush | Steel | -- | -- | 13 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | One per wall min. | -- | -- | F7, F4, F17, F8, F13 | Multilevel Switching (FL), Dimming (LED) | N/A | Under-cabinet task lights and desk lights shall be controlled with integrated switches. | 1 min.
DIGESTIVE DISEASES - ENDOSCOPY SERVICE | Endoscopy Procedure | Procedure Room, Endoscopy | Endoscopy Procedure | Procedure | WSF | WSF | GWB SC | -- | -- | -- | AT SP | 9'-0" | -- | 4'0" | Flush | Wood | -- | -- | 13AHS | -- | 68 | 73 | 50 | 30 | 10 | 2 | Exhaust (G) | 35 | (o) | -- | 7 | 1 | Ceiling Mounted Boom | ALL LEDs Two (2) Fixtures (2'x4') Ten (10) recessed can, down lights (dimmable) | Dimming (LED) | Variable 10-100fc | Under Cabinet Light. Room 3500k | 3 min on walls, Ceiling Mounted Boom, wall mounted telephone
DIGESTIVE DISEASES - ENDOSCOPY SERVICE | Endoscopic Ultrasound Procedure | Procedure Room, ERCP/Endoscopic Ultrasound | Endoscopy Procedure | Procedure | WSF | WSF | GWB SC | -- | -- | -- | AT SP | 9'-0" | -- | 4'-0" | Flush | Wood | -- | -- | 13AHS | -- | 68 | 73 | 60 | 30 | 6 | 2 | Return | 35 | (o) | -- | 7 | 1 | Ceiling Mounted Boom | ALL LEDs Two (2) Fixtures (2'x4') Ten (10) recessed can, down lights (dimmable) | Dimming (LED) | Variable 10-100fc | Under Cabinet Light. Room 3500k | 4 min on walls, Ceiling Mounted Boom, wall mounted telephone
DIGESTIVE DISEASES - ENDOSCOPY SERVICE | Scope Reprocess | Reprocessing Room, Scope | Instrument Processing room | -- | WSF | WSF | GWB SC | S | 5'-0" | -- | AT SP | 9'-0" | -- | 3'-6" | Flush | Wood | -- | -- | 34S | -- | 66 | 72 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (-) | -- | 6 | -- | Washer equipment may require hardwired connections. | ALL LEDs Two (2) Fixtures (2'x4'), Gasketed Lens | -- | -- | -- | 2 min, wall mounted telephone
DIGESTIVE DISEASES - ENDOSCOPY SERVICE | Prep and Recovery | Prep / Recovery Room | Pre-procedure patient care room | -- | WSF | WSF | GWB P | RWC | 4'-0" | -- | AT SP | 9'-0" | -- | 8'-0" | Sliding | Glass | Glass | -- | Push/Pull | -- | 75 | 70 | 60 | 30 | 6 | 2 | Return | 35 | (0) | -- | 7 | -- | -- | Two (2) 1'x4' One (1) recessed can | -- | -- | Patient Control for Multi-Function and Down Light Fixtures | 2 min, wall mounted telephone
SURGICAL SUITE | Pre-Operative Holding / Phase II Recovery Patient Bay | Patient Bay, Pre-Operative Holding / Phase II Recovery | Phase II recovery | -- | WSF | WSF | GWB SC | -- | -- | -- | AT SP | 9'-0" | -- | -- | Curtain | -- | -- | -- | -- | -- | 75 | 70 | 60 | 30 | 6 | 2 | Return | 35 | (+) | M28 | 8 | -- | emergency power required | -- | -- | VA Lighting Design Manual section 4.2.15 - Pre-Operative and Post- Anesthetic Care (PACU) | -- | 2 min, wall mounted telephone
SURGICAL SUITE | Pre-Operative Holding / Phase II Recovery Patient Room | Patient Room, Pre-Operative Holding / Phase II Recovery | Phase II recovery | Exam | WSF | WSF | GWB SC | -- | -- | 35 | AT SP | 9'-0" | -- | 8'-0" | Sliding | Glass | Glass | -- | Push/Pull | -- | 75 | 70 | 60 | 30 | 6 | 2 | Return | 35 | (+) | M28 | 8 | -- | emergency power required | -- | -- | VA Lighting Design Manual section 4.2.15 - Pre-Operative and Post- Anesthetic Care (PACU) | -- | 2 min, wall mounted telephone
SURGICAL SUITE | Anesthesia Clean Room | Clean Workroom, Anesthesia | -- | -- | RES | RES | GWB SC | -- | -- | -- | GWB SC | 9'-0" | -- | 3'-6" | Flush | Wood | -- | -- | 34S | -- | 75 | 70 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Individual room control | 6 | -- | -- | -- | -- | -- | Anesthesia Work Room has similar lighting design consideration as Exam & Treatment Room. Refer to the VA Lighting Design Manual section 4.2.1 - Examination and Treatment Room - for lighting design consideration. | 3 min.
SURGICAL SUITE | General Operating Room | Orthopedic Operating Room, Urology / Cystoscopy Operating Room, Cardiothoracic Operating Room, Cardiothoracic / Hybrid OR pump Room, Neurosurgical Operating Room, Robotics Operating Room, Transplant Operating Room, Monoplane Hybrid Operating Room, Biplane Hybrid Operating Room | Operating Room | Operating Room | RES | RES | GWB SC | -- | -- | -- | GWB SC | 10'-0" | -- | Double 6'-0" -------------- Single 4'-0" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 43LS --------------- 33AHLS | -- | 66 | 75 | 60 | 30 | 20 | 4 | Return | 40 | (++) | M20 | 17 | -- | Normal Power: Connect selected receptacles and equipment to Normal power IPS. Emergency Power:Connect selected receptacles and equipment to Critical Branch emergency IPS. Provide Isolation Power Supply, Lazer receptacle, connections for articulating utility columns. | -- | -- | -- | Refer to the VA Lighting Design Manual section 4.2.13 - Surgery/Operating Room - for lighting design consideration. | 3 min, wall mounted telephone
SURGICAL SUITE | Hybrid OR Control Room | -- | -- | -- | RES | RES | GWB SC | -- | -- | -- | GWB SC | 9'-0" | -- | 3'-0" -------------- 3'-0" | Flush w/ Narrow Vision | Wood | -- | -- | 33AHLS --------------- 43LS | -- | 75 | 70 | 60 | 30 | 8 | 2 | Return | 40 | (o) | VAV, individual room control. Unoccupied ACH 4 | 7 | -- | Emergency Power: Critical branch of the EES to be connected to selected receptacles and equipment. Notes: 1) Provide a duplex receptacle per computer and location connected to Emergency. 2) Provide convenience duplex receptacle on normal power. | -- | -- | -- | Refer to the VA Lighting Design Manual section 4.2.13 – Surgery/Operating Room – Design Parameter – Control Room - for lighting design consideration. | 6 min.
SURGICAL SUITE | Cardiac Catheterization Laboratory | -- | Laboratory work room | Procedure | RES | RES | GWB SC | -- | -- | -- | GWB SC | 10'-2" | -- | Double 6'-0" -------------- Single 4'-0" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 43LS --------------- 33AHLS | -- | 66 | 75 | 60 | 30 | 20 | 4 | Return | 40 | (++) | M21 Unoccupied ACH 10 | 24 | -- | Emergency Power: Connect selected recep tacles and equipment to Normal power IPS. Connect selected recep tacles and equipment to Critical Branch emergency IPS. Notes: 1) Provide IPS power & ground modules – 3 duplex receptacles & 3 ground jacks 2) IPS Power & ground modules mounted at +24” AFF 3) Provide Laser Receptacle Module. Module shall be connected to Special Equipment IPS located outside the Surgery Room. 4)Provide power connections for articulating utility columns. | -- | -- | -- | Refer to the VA Lighting Design Manual section 4.2.13 - Surgery/Operating Room - for lighting design consideration. | 11 min
SURGICAL SUITE | Electrophysiology Procedure Room | -- | Procedure Room | Procedure | RES | RES | GWB SC | -- | -- | -- | GWB SC | 10'-2" | -- | Double 6'-0" -------------- Single 4'-0" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 43LS --------------- 33AHLS | -- | 66 | 75 | 60 | 30 | 20 | 4 | Return | 40 | (++) | M21 Unoccupied ACH 10 | 22 | -- | Emergency Power: Connect selected recep tacles and equipment to Normal power IPS. Connect selected recep tacles and equipment to Critical Branch emergency IPS. Notes: 1) Provide IPS power & ground modules – 3 duplex receptacles & 3 ground jacks 2) IPS Power & ground modules mounted at +24” AFF 3) Provide Laser Receptacle Module. Module shall be connected to Special Equipment IPS located outside the Surgery Room. 4)Provide power connections for articulating utility columns. | -- | -- | -- | Refer to the VA Lighting Design Manual section 4.2.13 - Surgery/Operating Room - for lighting design consideration. | 9 min
SURGICAL SUITE | Transesophageal Echocardiograph (TEE) Procedure Room | -- | -- | Procedure | RES | RES | GWB SC | -- | -- | -- | AT SP | 9'-0" | -- | Double 6'-0" -------------- Single 4'-0" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 43LS --------------- 33AHLS | -- | 75 | 70 | 60 | 30 | 10 | 2 | Return | 35 | (-) | -- | 11 | -- | Normal Power: Emergency Power: To be connected to selected receptacles and equipment. Critical branch of the EES to be connected to selected receptacles and equipment. | -- | -- | -- | Refer to the VA Lighting Design Manual section 4.2.5 - Procedure Room - for lighting design consideration. | 6 min.
SURGICAL SUITE | TEE Probe Decontamination Room | Decontamination, TEE Probe | Decontamination Room | -- | RES | RES | GWB SC | -- | -- | -- | GWB SC | 9'-0" | -- | 3’-0” | Flush | Wood | -- | -- | 33AS | -- | 69 | 69 | 55 | 30 | 10 | 10 | Exhaust (G) | 40 | (--) | -- | 2 | -- | Normal Power: To be connected to selected receptacles and equipment. Emergency Power: Critical branch of the EES to be connected to selected receptacles and equipment. | -- | -- | -- | Refer to the VA Lighting Design Manual section 4.2.14 - Surgical Corridor and Scrub Area - for lighting design consideration. | --
SURGICAL SUITE | Clean TEE Probe Storage | Storage, Clean TEE Probe | Clean Workroom | -- | RES | RES | GWB SC | -- | -- | -- | GWB SC | 9'-0" | -- | 3’-0” | Flush | Wood | -- | -- | 34S | -- | 70 | 70 | 55 | 30 | 4 | 2 | Return | 35 | (o) | -- | 1 | -- | Normal Power: To be connected to selected receptacles and equipment. Emergency Power: Critical branch of the EES to be connected to selected receptacles and equipment. | -- | -- | -- | Refer to the VA Lighting Design Manual section 4.2.14 - Surgical Corridor and Scrub Area - for lighting design consideration. | --
SURGICAL SUITE | Phase I Recovery PACU Patient Bay | -- | Phase I recovery | -- | RES | RES | GWB SC | -- | -- | 35 STC (Room)/ None (Bay) | AT SP | 9'-0" | -- | -- | Curtain | -- | -- | -- | -- | -- | 75 | 70 | 60 | 30 | 6 | 2 | Return | 35 | (+) | -- | 7 | -- | Normal Power: To be connected to selected receptacles and equipment. Emergency Power: Critical branch of the EES to be connected to selected receptacles and equipment. | -- | -- | -- | Refer to the VA Lighting Design Manual section 4.2.15 - Pre-Operative and Post-Anesthetic Care (PACU) - for lighting design consideration. | 1 min.
SURGICAL SUITE | Airborne Infection Isolation (AII) Phase I Recovery PACU Patient Room | -- | AII room | Exam | WSF | WSF | GWB SC | -- | -- | 35 STC (Room)/ None (Bay) | AT SP | 9'-0" | -- | 8'-0" | Sliding | Glass | Glass | -- | Push/Pull | -- | 75 | 70 | 60 | 30 | 12 | 2 | Exhaust (S) | 35 | (--) | Unoccupied ACH 6 | 9 | -- | Normal Power: To be connected to selected receptacles and equipment. Emergency Power: Critical branch of the EES to be connected to selected receptacles and equipment. | -- | -- | -- | Refer to the VA Lighting Design Manual section 4.2.15 - Pre-Operative and Post-Anesthetic Care (PACU) - for lighting design consideration. | 1 min.
SURGICAL SUITE | Airborne Infection Isolation (AII) Phase I Recovery PACU - Ante Room | -- | -- | -- | WSF | WSF | GWB SC | -- | -- | 35 STC (Room)/ None (Bay) | AT SP | 9'-0" | -- | 3'-0" | Flush | Wood | Narrow Vision | -- | 12S | -- | 75 | 70 | 60 | 30 | 10 | 2 | Exhaust (S) | 35 | (-) | Unoccupied ACH 6 | 1 | -- | -- | -- | -- | -- | -- | 1 min.
SURGICAL SUITE | Frozen Section Laboratory | Laboratory, Frozen Section | Laboratory work room | -- | PT RES | RES | GWB SC | -- | -- | -- | GWB SC | 9'-0" | -- | 3'-0" | Flush | Wood | -- | -- | 34S | -- | 75 | 70 | 60 | 30 | 6 | 2 | Exhaust (G) | 40 | (-) | - | 5 | -- | Normal Power: To be connected to selected receptacles and equipment. Emergency Power: Critical branch of the EES to be connected to selected receptacles and equipment. Notes: 1) Connect lab equipment to Critical Branch of the EES. | -- | -- | -- | Refer to the VA Lighting Design Manual section 4.2.4 - Laboratory - for lighting design consideration. | --
SURGICAL SUITE | Surgical Soiled Utility Room | Utility Room, Soiled | Soiled holding | -- | WSF | WSF | GWB Epoxy | RWC | 4'-0" | -- | GWB SC | 9'-0" | -- | 3'-0" | Flush | Wood | -- | -- | 121S | -- | -- | -- | -- | -- | -- | -- | Exhaust (G) | 45 | (--) | M23 | 1 | -- | Normal Power: To be connected to selected receptacles and equipment. Emergency Power: Not required. | -- | -- | -- | Refer to the VA Lighting Design Manual section 7.3 - Soiled Utility Room - for lighting design consideration. | 1 min.
SURGICAL SUITE | Clean Core | Clean Core, Surgical Services | Clean Workroom | Corridor | RES | RES | GWB SC | -- | -- | -- | GWB SC | -- | -- | Double 6'-0" | Flush | Wood | Narrow Vision | -- | 44AS | -- | 75 | 70 | 60 | 30 | 8 | 2 | Return | 40 | (+) | M24 | -- | -- | -- | -- | -- | -- | -- | --
SURGICAL SUITE | Heart Lung Machine Preparation | PUMP ROOM, CARDIOTHORACIC/HYBRID OR | -- | -- | RES WSF | RES WSF | GWB SC | RWC | 4'-0" | -- | GWB SC | 9'-0" | -- | 4'-0" | Flush | Wood | -- | -- | 34AS | -- | 75 | 70 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Unoccupied ACH 3 | 5 | -- | Normal Power: To be connected to selected receptacles and equipment. Emergency Power: Critical branch of the EES to be connected to selected receptacles and equipment. Notes: 1) Provide a duplex receptacle per computer and equipment location connected on emergency. 2) Provide convenience duplex receptacle on normal power. | -- | -- | -- | Refer to the VA Lighting Design Manual section 7.10 - Equipment Room - for lighting design consideration. | 2 min.
SURGICAL SUITE | Semi-Restricted Corridor | Clean Core, Surgical Services | -- | Corridor | RES | RES | GWB SC | -- | -- | -- | GWB SC | -- | -- | Double 6'-0" | Flush | Wood | Narrow Vision | -- | 44AS | -- | 75 | 70 | 60 | 30 | 8 | 2 | Return | 40 | (o) | M24 | -- | -- | -- | -- | -- | -- | -- | --
Note on K34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: find out how booths are specified and what is the min requirement for VA.

## Interior Finishes Notes
Interior Finishes Notes
General Notes
A. | Hollow metal frames and doors to be painted.
B. | Window sills to be solid surface fabrication.
C. | Resilient base to be 4", unless otherwise noted.
D. | Provide painted finishes only on inside of exterior walls (no wall covering).
E. | Floor material transitions to occur at centerline of door, unless otherwise noted.
F. | Wall brackets, grills, fire extinguisher cabinets, fin tube radiation, etc. to be painted to match adjacent wall color.
G. | Interior stairwell treads to be concrete with rubber nosings and RFT, LVT or RF landings. Stair nosings to be a contrasting color for safety.
H. | Coordinate height of wall protection with wall-mounted devices.
I. | Gypsum board soffits may be substituted for ACT above locations such as nurse stations, patient transaction/consultation desks, reception desks and
lobby/waiting areas.
J. | Soffit above upper cabinets to be gypsum board.
K. | Refer to FGI recommendations regarding indoor air quality, sustainability and life cycle of materials.
L. | Solid surface countertops to have sides and backsplash at walls.
Schedule Notes
1. | CT tile to 7'-0" on plumbing and adjacent wall(s) with paint above to ceiling.
2. | Tile base to be coved.
3. | Integral coved base 6" high tightly sealed to walls.
4. | If sink is present, use hard suface flooring as noted.
5. | Lead lined walls and control area view window.
6. | Flooring and base to match adjacent area flooring material and base.
7. | Use gasketed, clip down ACT/grid system
8. | Use slip-retardant finish on floor material
9. | Public and exposed open stairways to be treated similar to adjacent spaces using CT/PT/RF on treads. Stair nosings to be a contrasting color for safety.
10. | Note that if wall saver designed chairs are used, no wall protection is required.
11. | Extend all room partitions to structural deck.
12. | CT above countertop on wall.
13. | Ceiling height as required to acommodate equipment.
14. | Cove QT base, 6" high.
15. | No separate trim at top of base, use alternate method to seal to wall.
16. | Ceiling suspension system should be fabricated from nonferromagnetic material.
17. | Aesthetic specialty materials may be used as accents where the design and budget permits.
18. | Ceiling tile to meet USDA regulations.
19. | Floors to be slip-resistant and meet ANSI 326.3 for measuring dynamic coefficient of friction for hard surfaces
20. | Wall base on gyp board but not needed on any exterior materials such as brick, metal, or stone walls.
21. | Wall CT and ceiling to meet building code light reflectancy standards.
22. | Space may be room or area within a room. Coordinate finishes with adjacent spaces.
23. | Provide 3/4" painted plywood where required by Telecommunications.
Finish Codes
AT | Acoustical Ceiling Tile
AT-SP | Acoustical Scrubbable Ceiling Tile (with sprayed plastic finish)
CPT | Carpet Tile
CS | Concrete, Sealed
CT | Ceramic Tile (Wall)
EP | Epoxy Paint
EXP | Exposed Ceiling
MAT | Modular Carpet Walk Off Mat
P | Paint
PT | Porcelain Tile
QT | Quarry Tile
RB | Resilient Base
RES | Resinous Flooring and Base
RF | Rubber Flooring
RFT | Resilient Floor Tile
RSF | Resilient Sheet Flooring - Heterogeneous
RWC | Rigid Wall Covering (Wall Protection)
SD | Static Dissipative Tile
S | Solid Surface Fabrication
WSF | Welded Seam Sheet Flooring - Homogeneous

## Doors and Hardware Notes
Doors and Hardware Notes
General Notes
A. | Refer to Lease Design Narrative (LDN) Appendix for Hardware Groups and Modifiers which are added to numeric hardware group assignments to indicate a variation to
the group.
B. | All doors to be 7'-0" high, unless otherwise noted.
C. | Coordinate acoustical requirements for doors with required wall acoustical ratings as shown in Room Data Matrix - Interior Finishes in Appendix.
Schedule Notes
1. | Hollow metal frame cased opening
2. | Two door (in swing and swing out) acoustical door and frame assembly.
3. | Two doors required at this room/space.
4. | Narrow lite optional. Use insulated or laminated glass to meet acoustical criteria.
5. | Provide STC 50 rated acoustical door.
6. | No door in this room/space.
7. | Equal leaf pair of doors.
8. | Lead lined door and hardware.
9. | Space may be a room or area within another room. Omit door if space is not a separate room.

## Electrical Notes
ELECTRICAL NOTES
POWER NOTES |  | LIGHTING NOTES
P1. | Multiple receptacles above and below desk for device charging, receptacles provided with Pre-Fab system. | L1. | EMI/RFI emissions to be controlled
P2. | Receptacles on all walls | L2. | Dimmable to 5 fc
P3. | Coordinate electrical connections with equipment to be installed. Receptacles on all walls. | L3. | May not have ceiling - then use industrial fixture type
P4. | Plug strip at 44" above counters | L4. | May not have ceiling. If no ceiling, use industrial fixture type
P5. | Multiple receptacles above and below desk for device charging | L5. | Treat like a store. Adjustable lighting, General lighting.
P6. | Cord reel(s) for freestanding workbenches | L6. | No ceiling in these rooms. No prescription for lighting.
P7. | All outlets on dedicated circuits.
P8. | Cord reel(s) for freestanding workbenches
P9. | Treadmill on dedicated circuit
P10. | Each hood on dedicated circuit
P11. | Provide receptacles per equipment plan
P12. | Electrical to review redundancy requirements with OIT guidelines.
P13. | Receptacle above ceiling for overhead lift
P14. | Recessed power quad floor box
P15. | L21-20R receptical above each rack
P16.

## Fixture Type Notes
FIXTURE TYPE & CONTROLS NOTES
FIXTURE NOTES
F1. | Recessed ceiling-mounted CFL or LED downlight.
F2. | Wall-mounted CFL, FL or LED mirror or vanity luminaire.
F3. | Recessed wall-mounted amber LED night light.
F4. | Recessed ceiling-mounted CFL or LED downlight or wall washer.
F5. | Decorative CFL, FL or LED wall-mounted sconce.
F6. | Stand-mounted CFL or LED table or floor lamp.
F7. | Recessed ceiling-mounted FL or LED lensed luminaire.
F8. | Recessed ceiling-mounted FL or LED cove or perimeter light.
F9. | Decorative CFL, FL or LED wall-mounted sconce or ceiling-mounted pendant.
F10. | Heat lamps.
F11. | Linear suspended FL or LED indirect/direct luminaire.
F12. | Linear wall-mounted FL or LED indirect/direct luminaire.
F13. | Surface-mounted FL or LED under-cabinet task light (if not provided with pre-fabricated furniture system).
F14. | Recessed or surface ceiling-mounted FL or LED lensed light fixture.
F15. | Surface or suspended ceiling-mounted FL or LED industrial fixture.
F16. | Wall-mounted FL or LED industrial fixture.
F17. | Suspended linear FL or LED indirect/direct luminaire.
F18. | Recessed ceiling-mounted fluorescent or LED cove or perimeter light.
F19. | Wall-mounted FL or LED movable dock light.
F20. | Track-mounted LED accent or flood light.

## Mechanical Notes
MECHANICAL HVAC NOTES
M1. | Intentioanlly Left Blank
M2. | Per ASHRAE 62 for ventilation, and FGI Guidelines for NC
M3. | General Open Office area
M4. | General Open/Public area
M5. | Per ASHRAE 62 for ventilation if interior enclosed space.
M6. | Comply with ASHRAE 15 if Special Refrigeration Systems are used
M7. | If chemicals are used, provide specialized exhaust
M8. | Data Center
M9. | Transfer air to Food Prep Kitchen
M10. | Intentioanlly Left Blank
M11. | MEP Room
M12. | See USP-797 and -800
M13. | Counter-height specialized exhaust system required
M14. | Provide air conditioning and ventilation per imaging manufacturer recommendations
M15. | General Office Area
M16. | Verify specific vendor/manufacturer requirements.
M17. | Non-ferrous construction
M18. | Provide cooling only air terminal unit to serve the manual equipment wash room.
M19. | Provide a dedicated wet exhaust system
M20. | General Requirement: Refer to data sheet in the current version of the VA HVAC Design Manual for room temperatures, humidity range, room air change requirements, and pressurization Notes: 1) Refer to the HVAC Design Manual for number and location of low air return grilles. 2) Room does not contain multiple slot diffusers and uses laminar flow perforated face outlets only for supply air. 3) Suggested minimum laminar flow array over the entire sterile field area as imaging equipment gantry creates excessive turbulence. Mechanical design engineer shall be responsible to design the array in such manner as to minimize turbulence and to maintain the sterile aseptic field.
M21. | General Requirement: Refer to data sheet in the current version of the VA HVAC Design Manual for room temperatures, humidity range, room air change requirements, and pressurization Notes: 1) Refer to the HVAC Design Manual for number and location of low air return grilles. 2) Room does not contain multiple slot diffusers and uses laminar flow perforated face outlets only for supply air. 3) Suggested minimum laminar flow array over the entire sterile field area as imaging equipment gantry creates excessive turbulence. Mechanical design engineer shall be responsible to design the array in such manner as to minimize turbulence and to maintain the sterile aseptic field.
M22. | Room Exhaust. Transfer room air to the Sterilizer Equipment Room and connect to the general exhaust system. This room is positive with respect to the equipment room.
M23. | Room Exhaust. Transfer air from the adjoining spaces for exhaust.
M24. | Air Balance. Negative with respect to the Operating and Cystoscopy Rooms during occupied and unoccupied modes of operation.
M25. | Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation.
M26. | Room Air Balance. Positive during occupied and unoccupied modes of operation.
M27. | Room Air Return. Return air is not permitted if chemicals are used in film processing.
M28. | Size reheat coils to allow space heating to 86F / 30 C in demand.