## Respondants (hidden)
|  | Response | Completed |  | Finalized
Intro |  |  | 2020-06-10 | Koch | Yes
Overview |  |  | 2020-06-10 | Koch | Yes
General |  |  | 2020-06-10 | Koch | Yes
| BIM |  | 2020-09-28 | Yo | Yes
| SPECS | 2020-06-18 | 2020-06-18 | Johnson | Yes
| CPM | 2020-06-12 | 2020-06-12 | Ghobanpour | Yes
| CX | 2020-06-11 | 2020-06-18 | Tash | Yes
Civil |  | 2020-06-24 | 2020-06-24 | Symanski | Yes
Structural |  |  | 2020-09-17 | Doiron | Yes
Structural |  | 2020-06-18 | 2020-06-18 | Archilla | Yes
Structural |  | 2020-07-29 | 2020-09-17 | Ghosh | Yes
Architecture |  |  | 2020-06-18 | Koch | Yes
Architecture |  | 2020-06-12 | 2020-06-12 | Treece | Yes
Equipment |  | 2020-06-18 | 2020-06-18 | Brown | Yes
Interiors |  | 2020-07-07 | 2020-07-07 | Burdiak | Yes
Fire |  | 2020-04-24 | 2020-04-24 | Larrimer | Yes
Plumbing |  | 2020-06-18 | 2020-06-18 | Desai | Yes
Mechanical |  | 2020-06-24 | 2020-06-24 | Raychaudhri | Yes
Mechanical |  | 2020-06-18 | 2020-06-18 | Walden | Yes
Elect |  | 2020-05-13 | 2020-05-13 | Tran | Yes
Elect |  | 2020-06-18 | 2020-06-18 | Lau | Yes
Telecom |  | 2020-06-11 | 2020-06-12 | Bates | Yes
Telecom |  | 2020-06-11 | 2020-06-12 | Frakes | Yes
Environmental |  | 2020-06-18 | 2020-06-18 | Elliott | Yes
Sustainable |  | 2020-06-24 | 2020-06-24 | Symanski | Yes
Historic |  | 2020-06-18 | 2020-06-18 | Abreu | Yes
Physical Security |  | 2020-06-18 | 2020-06-18 | Lau | Yes
Elevator |  | 2020-06-24 | 2020-06-24 | Phillips | Yes
Cost |  | 2020-06-18 | 2020-06-18 | Hoover | Yes
Yes
100%

## Introduction
2020-11-01
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
A. | How to Use this Document
| 1. | At the top of the Heading in the GENERAL Tab, enter the Project Name, Project Number, and AE Contract Effective Date.
| 2. | This spreadsheet shall be used to ensure all required content is delivered to VA at indicated milestones.
| 3. | VA will use this document as a review tool to ensure all deliverables are addressed.
| 4. | The PG 18-15 spreadsheet for the required design deliverables should be finalized for the project by the VA and the AE during an assessment phase prior to the project kickoff meeting.
| 5. | Each Tab represents a typical discipline(s) used on a VA project. It remains the responsibility of the AE to coordinate disciplines (e.g., sustainability, cost estimating, building systems, etc.) regardless of where the deliverables are listed in the spreadsheet discipline tabs.
| 6. | The PG 18-15 spreadsheet is locked with the exception of the Submittal Checklist section. Rows can be inserted to the spreadsheet when additional work is required for a project.
| 7. | Work that is not needed can be eliminated by putting "NA" in the appropriate Submittal Checklist column.
| 8. | PHASE: Each Design delivery phase has a column:
C = Conceptual Design
SD1 = Schematic Design
SD2 = Schematic Design (35%)
DD = Design Development
CD = Construction Documentation
In each phase, the level of development for each submittal element is defined. The levels are:
P = Preliminary Information
U = Updated Information
F = Final Information
R = Resubmission
| 9. | SUBMITTAL CHECKLIST HEADER: The AE should place an "X" in the appropriate Submittal Checklist section (Submitted, Pending, Not Applicable (NA)) to note the status and inclusion of the content in the submittal. Include the location of the submittal where the information can be found. Comments may be noted if explanations are needed.
| 10. | Type of Deliverable
Report
Calculations
Aggregate (a mix of deliverable types)
Drawings (BIM and 2D Documentation)
| 11. | The PG 18-15 Checklist for the project must be provided in the latest version of Excel, and also printed and included at the front of the Submittal Deliverable.
| 12. | The Excel file must be saved using the official project name and submittal phase. Example: Jefferson Davis Towers-SD1.xlsx
B. | Table of Contents
Overview
General
Integrated Project Design
Building Information Model
Specifications
Critical Path Method
Commissioning
Civil
Structural
Architectural
Medical & Food Equip.
Medical Equipment
Food Service
Interiors
Interiors
Furniture Fixtures & Equipment
Signage & Wayfinding
Fire Protection
Plumbing
Mechanical
Heating, Ventilating & Air Conditioning
Steam Generation (Outside)
Steam Generation
Incineration / Waste Disposal Systems
Electrical
Telecommunications
Environmental Compliance
Sustainability
Historic
Physical Security
Elevator Transport
Cost Estimating
C. | Header Legend
VA SME Michael Koch 202-632-5236
michael.koch3@va.gov

## Overview
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT BOOK PHASE (For Information Only)
General
|  | 1 | The purpose of the PROJECT BOOK analysis phase is to provide a thorough technical evaluation to establish the requirements for the project, covering site and any existing building conditions, utilities, the final SEPS Program for Design (PFD) baseline and Preliminary Room Contents (PRC), which will establish the Design-to Budget for the AE of Record. The PROJECT BOOK analysis will be done under a separate contract from the AE-of-Record contract.
|  | 2 | Additional studies may be required to verify existing conditions to resolve proposed programming issues. Special studies shall be handled on a case-by-case basis with the approval of the VA PM. AE will verify and coordinate workload and staffing requirements.
|  | 3 | The PROJECT BOOK includes only studies and analysis; it does not include any design work.
|  | 4 | The PROJECT BOOK will be provided to the AE of Record to be the basis of the design work
I. |  |  | DESIGN PHASE OVERVIEW
General
|  | 1 | The PG 18-15 requirements formatted by technical discipline does NOT direct the staffing of the work effort.
|  | 2 | This document contains the minimum submission requirements for the Design Phase of the major project.
|  | 3 | The Department of Veterans Affairs (VA) may contract for any portion of a design: Project Book, Concepts, Schematic Design, Design Development, Construction Documents, or a combination of these.
|  | 4 | The AE of Record is responsible for producing a complete set of construction instructions, including 3D models (BIM), drawings, specifications, calculations, sample boards, equipment catalog cuts, performance curves, dimensions, and capacity ratings, and data (from BIM, etc.) in accordance with VA criteria and national codes. The AE shall be responsible for obtaining and using all VA design criteria and information available through the VA Office of Construction & Facilities Management (CFM) Technical Information Library (TIL) website.
|  | 5 | The AE must use, manage, and submit all graphic/data information as described in the VA BIM STANDARD.
|  | 6 | All previously submitted documents shall be updated to reflect review comments and further development.
|  | 7 | The AE, in collaboration with the VA PM, will document all applicable codes standards in effect at the time of the contract award. This record will include a listing of all industry codes and a downloaded copy of VA applicable criteria, standards, design guides and design manuals, to be preserved on a DVD and be submitted to VACO, VA PM and others as identified by the VA PM.
|  | 8 | CFM (or Construction Agent) shall be responsible for reviewing and commenting on all design submissions. VA may engage the services of peer reviewers to review the submissions and a value management workshop may be performed at each review stage. (Peer reviewers’ comments shall be entered into the DrChecks system three working days prior to review; VA comments shall be entered in DrChecks no later than five working days after the review.) The A/E shall not move forward into the next design phase until comments in DrChecks have been resolved and the AE is instructed to proceed by the VA Project Manager (or Construction Agent).
|  | 9 | The AE will provide: one Conceptual (C) submission, two Schematic Design (SD1 & SD2) submissions, one Design Development (DD) submissions, and one Construction Document (CD) submission described in this document. At each submission, all material must be dated and provided to VA as per the VA BIM Standards (for 3D Models and 2D Drawing Deliverable Requirements (DDR), FM Data, etc.).
|  | 10 | The A/E shall provide individually packaged submissions to each unit specified in the "Distribution of Submission Materials" section. The AE will submit a completed check-list at each submission detailing all required submittal material by discipline. Any material not submitted will be marked either "Pending" with an anticipated date of submittal or "N/A", and include an explanation in the comments section.
|  | 11 | At each design phase the AE will provide a summary outlining substantive design changes, and any deviations from VA Criteria such that VA reviewers can easily evaluate the proposed changes. Deviations from VA Criteria must include a reference to the VA Criteria, the proposed deviation, and AE justification for the deviation including cost implications, to be evaluated by the PM and VACO/CSS prior to implementation. The AE must keep a log of all deviation requests.
|  | 12 | VA will conduct design reviews for the following submissions:
Concept Design (C) Held at VACO Offices, Washington DC unless otherwise directed by USACE.
Schematic Design 1 (SD1) Held at VACO Offices, Washington DC otherwise directed by USACE.
Schematic Design 2 (SD2) Held at VACO Offices, Washington DC otherwise directed by USACE.
Design Development (DD) Held at VACO Offices, Washington DC otherwise directed by USACE.
Construction Documents (CD) Location TBD
|  | 13 | The VA CPM group shall review all CPM schedules, and monthly updates throughout the project development and construction.
|  | 14 | The AE must identify potential alternates for bidding development. The value of the deduct alternates shall represent at least 10% of the construction budget.
|  | 15 | For seismic retrofit projects funded by Seismic EQ funds: Project shall seismically upgrade the facility in accordance with VA standards and criteria. Other functional, programmatic and physical upgrades shall be limited to the minimum changes necessary to accomplish the implementation of the seismic corrections.
II. |  |  | CONCEPT DESIGN [C]
GENERAL
|  | 1 | Before the concepts are created, the AE must work with the user groups to identify no less than five key criteria for evaluating the alternatives, which will be placed into a scaled (1-5 with 5 the highest score) decision matrix. The primary criterion should be Medical Functionality.
|  | 2 | The purpose of Conceptual Design is to develop three distinct solutions for meeting the objectives outlined in the PROJECT BOOK. Each solution must show (at a departmental/building block massing level in BIM) departmental adjacencies, vertical (stairs and elevators) and horizontal circulation, stacking diagrams, and site placement/access and circulation. Renderings must convey design intent using minimum embellishment. All three concepts must be at the same level of development. VA reserves the right to reject concepts that are not fully developed with respect to the overall submittal. VA will select the preferred concept considering the evaluation criteria developed before the Conceptual Design Phase.
III. |  |  | SCHEMATIC DESIGN [SD]
GENERAL
|  | 1 | The Schematic Design phase documents are developed for the VA-selected concept approved in the Conceptual Design phase. Schematic Design further develops the concept plan to a level of detail that includes specific functional and adjacency requirements and establishes the aesthetics of the design.
|  | 2 | A Project Management Plan shall be developed by the Integrated Project Team, led by the VA PM.
|  | 3 | Graphic submittals must follow the VA BIM Standards. All models, drawings, booklets, and other supporting materials in each submittal shall be clearly and consistently identified throughout the design process with the project title, location, building, phase, section, and segment. Written materials must refer back to the PG 18-15 corresponding numerical description.
|  | 4 | Specifications shall be prepared using VA Master Construction Specifications. Submissions shall show changes to master by using the "Track Changes" function. Each submission shall indicate changes from previous submission, not all changes to the master. Specifications submitted at the end of each phase (not for each review) shall include all changes.
|  | 5 | The A/E shall submit minutes of meetings with VA and VA's other contractors, as well as for A/E coordination meetings.
|  | 6 | Each progressive design submittal should build upon the previous information to provide a clear basis of design development and design philosophy fitting to the project.
IV. |  |  | DESIGN DEVELOPMENT [DD]
GENERAL
|  | 1 | The Design Development phase encompasses adding an increased level of detail for all aspects of the project to further define the design. Submissions at this stage must show coordination of trades and clarity of scope and design intent. The AE will perform a room test-fits to assure that all required Project Room Contents (PRC) can be accommodated. Submissions at this stage must show coordination of trades and clarity of scope and design intent. This phase will also provide visualization of the project and communicate the character of interior and exterior spaces. All value engineering shall be completed by the end of this phase, and no functional changes are anticipated after the DD review.
Specifications shall be prepared using VA Master Construction Specifications. Submissions shall show changes to master by using "Track Changes" function. Each submission shall indicate changes from previous submission, not all changes to master.
V. |  |  | CONSTRUCTION DOCUMENTS [CD]
GENERAL
|  | 1 | The purpose of the Construction Document phase is to add the level of detail required for construction of the project, coordinate the trades, and finalize the project’s documentation for construction. This includes refinement of the 3D Models, 2D drawings, design details, and specifications so the project can achieve its highest value and performance suitable for the building's lifecycle.
|  | 2 | The Construction Document phase involves the production of complete 3D Models, 2D drawings, specifications, and other documents necessary for the bidding and construction of the project, prepared from the approved DD documents. Also included at this phase are the final cost estimate, the final phasing plan, and the construction schedule.
|  | 3 | The A/E must provide design-intent documentation that provides the necessary information for construction. Documentation shall be complete, fully coordinated, and ready for use by a General Contractor.
|  | 4 | Prior to issuance for construction bids, make any changes to the documents identified as necessary during the review conference with VA Central Office.
|  | 5 | The final specification submission must be complete and coordinated with the graphic documentation (3D models, 2D Drawings). The final submission must be a "clean copy" and not show changes.
|  | 6 | Identify the alternates for bidding development. The value of the deduct alternates shall represent at least 10% of the construction budget.
All construction documents and calculations must be signed and sealed by a professional AE at the 100% submission.
VI. |  |  | DISTRIBUTION OF A/E SUBMITTALS FOR REVIEW
| A. |  | GENERAL
|  | 1 | See table below:
VA SME Michael Koch 202-632-5236
michael.koch3@va.gov

## General
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET / AE CONTRACT
2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | GENERAL |  |  |  |  | General Requirements per subheadings below
G-1.0 | Report |  | Integrated Project Design
G-1.1 | Report |  |  |  | Integrated Project Team (IPT) Directory |  | Submit Integrated Project Team (IPT) directory: List of team members, contact information, roles, and responsibilities. Include as appropriate: VA's representatives/stakeholders, A/E, Commissioning Agent, designated subcontractors, community representatives, regulatory agencies, and consultants for specialty disciplines such as Traffic Engineer, Geotechnical Engineer, Environmental Engineer, automatic transportation, blast, Cost Estimate/Management, Acoustical, BIM Manager, and Historic Preservation. Update Team Directory at subsequent phases notifying VA of changes. | P | U | U | U | F
G-1.2 | Report |  |  |  | Quality Control Plan |  | Submit a Quality Control Plan 30-days after award. Demonstrate that the project plans and specifications have gone through a rigorous review and coordination effort. Provide an outline of the actions that the firm will take during the design process. Include each step that will be taken during the development of the various phases of design. Include BIM Design Coordination activities in the QA plan. Review to be conducted by a senior member of the firm who can initial and date when the action has been completed. | P | U | U | U | F
G-1.3 | Report |  |  |  | Certification of Independent Technical Review and Quality Assurance Review |  | Submit form indicating certification of an ITR and Quality Assurance Review |  | F | F | F | F
G-1.4 | Report |  |  |  | Project Management Plan (PMP) |  | Provide support, input, information, data, and detail to the VA Project Manager for development of the VA Project Management Plan (PMP) which will address Scope/Requirements, Schedule, Cost Management, Communications Management, Process Improvement, Staffing Management, Quality Management, Change Management, and Risk Management, and cover functionality, budgetary, aesthetic, sustainability, security, schedule, procurement method, and related requirements for the project. The VA PMP shall also outline participants roles and responsibilities, regularity of meetings, and define the process for information sharing and frequency. The AE shall assist the VA PM in updating the PMP at each design phase. | P | U | U | U | F
G-1.5 | Report |  |  | Cost Estimation Integration Plan |  |  | Conduct a design cost reconciliation meeting before each phased deliverable. Cost Estimator shall be included in weekly team meetings. | P | U | U | U | F
G-1.6 | Report |  |  | Risk Mitigation Plan |  |  | Provide a Risk Mitigation Plan to address risks such as schedule delays, budget overruns, and scope changes. |  | P | U | U | F
G-2.0 |  | BUILDING INFORMATION MODELING
G-2.1 | Report |  |  | BIM Execution Plan (BxP) |  |  | Submit a Project Bim Execution Plan (BxP), including Data Security Plan, for the project as per VA BIM Standard. | P | U | U | U | F
G-2.2 | Report |  |  | BIM Geo-Referencing |  |  | Locate Model(s) according to VA BIM Standard Appendix - 5 | F
G-2.3 | Report |  |  | Space Reservations |  |  | Provide a report defining the space reservations required for each system and equipment. List equipment and system by name, the size and location of the space reservation, the required use for the space reservation, and the tools and equipment that will be used in the space reservation. |  |  | P | U | F
G-2.4 | Report |  |  | Interference Management (Design Coordination) |  |  | Provide summary report of design coordination conflicts remaining to be resolved for building components, equipment, systems, including those in interstitial space and underground utilities. Include insulation, pipe slope, and space reservations in interference management reviews. |  |  | P | U | F
G-2.5 | Report |  |  | Design Coordination Reach out Reports |  |  | Invite the project Constructability Reviewers to observe the Design Coordination meetings. Conduct BIM walk-throughs of all the building systems with the Medical Center Chief Engineer and CSS and others to obtain acceptance of maintenance access and function ability. Provide report of the date of the invitations, invitee name(s), attendee name(s), date of Design Coordination meeting, meeting minutes of results of activities. |  |  | P | U | F
G-2.6 | Report |  |  | Design Coordination Reports |  |  | Provide report of Design Coordination conflicts remaining to be resolved for building components, equipment, systems, including those in interstitial space and underground utilities. Include insulation, pipe slope, and space reservations in all interference management reviews. Provide line progression graph showing progress of all conflict resolutions over time. |  |  | P | U | F
G-2.7 | Report |  |  | Spatial & Equipment Data |  |  | Provide progress report on data accumulation (See VA BIM Standard Appendix 3) in Excel format. |  |  |  | P | F
G-2.8 | Report |  |  | Certification of integrity of space reservations |  |  | Provide certification that no space reservations have been encroached upon at completion of CDs. |  |  |  |  | F
G-2.9 | Report |  |  | Model Compliance Report QA/QC Report |  |  | Submit a QA/QC report that certifies the models are compliant with VA BIM Standard and the project requirements. |  | P | U | U | F
G-2.10 |  |  | Drawing/Model Deliverables |  |  |  | Files formats as described in VA BIM Standard
G-2.11 | Report |  |  | Laser Scans |  |  | See VA BIM Standard Deliverables | F
G-2.12 | Drawings |  |  | Blocking and Stacking, Phasing |  |  | See VA BIM Standard Deliverables | F
G-2.13 | Report |  |  | FM Data |  |  | Excel / COBie format. |  | P | U | U | F
G-2.14 | Drawings |  |  | Design-Intent Drawings |  |  | Design-Intent Drawings (derived from Model) |  | P | U | U | F
G-2.15 | Drawings |  |  | Design-Intent Model(s) |  |  | Native Format, NWD (or Equal); DWG, digital 2D PDF |  | P | U | U | F
G-2.16 |  |  |  | Signed and Sealed Models and Drawings |  |  | Final Models and Drawings shall be signed and sealed by a professional AE licensed in the geographic jurisdiction of the project. |  |  |  |  | F
G-2.17 | Drawings |  | Final Deliverables
G-2.18 | Drawings |  |  | As-Built Drawings |  |  | Provide Prior to Beneficial Occupancy.
G-2.19 | Drawings |  |  | FM Model |  |  | Provide Prior to Before Beneficial Occupancy.
G-2.20 | Report |  |  | Linking Electronic Files for Building Equipment/Systems |  |  | Linked and uploaded to Maximo to be provide prior to Beneficial Occupancy.
G-2.21 | Report |  |  | FM Data |  |  | Final upload to Maximo with AE supplied BIM viewer to be provided prior to Beneficial Occupancy.
G-3.0 |  | SPECIFICATIONS
G-3.1 | Report |  | Outline |  |  |  | Submit hyperlinked Table of Contents of applicable specification sections. Provide outline specification sections for building exterior materials and typical interior materials, using the “Track Changes” function. |  |  | P | U | F
G-3.2 | Report | [5 empty] | Submit outline specifications for all disciplines using “Track Changes” function. At SD2 provide Outline Specifications. Lists all proposed specifications to be used and identify any special specifications required for the project. |  | P | F
G-3.3 | Report | [5 empty] | Specifications for all technical disciplines shall be prepared using VA Master Construction Specifications. Where subsystems are performance specified, ensure that adequate design parameters are provided on drawings and/or specifications, that design responsibility (e.g. subsystem design by subcontractor's engineer) is clearly delineated, and that required submittals allow for review of subsystem design before fabrication. Submissions shall show changes to master by using "Track Changes" function. The CD2 submission shall not show changes. |  |  | P | U | F
G-3.4 | Report | [5 empty] | Prepare specifications that define the contractor's responsibility for BIM deliverables as outlined in the VA BIM STANDARDS, including Construction Coordination activities. |  |  | P | U | F
G-3.5 | Report | [5 empty] | Submit fully coordinated documents with other design disciplines suitable for bidding and approval by Authorities Having Jurisdiction. The specifications should be considered 100% complete with no additional coordination or information required. |  |  |  |  | F
G-3.6 | Report | [5 empty] | Provide Final Project Manual with signature and seal of architect of record on the cover. |  |  |  |  | F
G-4.0 |  | CRITICAL PATH METHOD
G-4.1 | Report |  | Construction Phasing Plan |  |  |  | Include phasing narrative in the Basis of Design for the final submission. | P | U | U | U | F
G-4.2 | [6 empty] | Provide phasing plans and 4D BIM. Coordinate with Architecture. |  |  | P | U | F
G-4.3 | Drawings | [5 empty] | Provide CPM Phasing Plan diagram (see CPM Design manual in TIL). | P | U | U | U | F
G-4.4 | Drawings | [5 empty] | Written list and drawings of systems, organized by technical disciplines, including temporary systems, swing spaces, etc. by phase. |  | P | U | U | F
G-4.5 | Aggregate |  | Concept Master Schedule Analysis |  |  |  | For each concept, prepare an schedule analysis showing the durations and impact of changes to the Overall Master Schedule prepared during Project Book. | F
G-4.6 | Aggregate |  | Project Master Schedule |  |  |  | Create a Project CPM Schedule based on the selected concept. Identify conditions that influence the Project Schedule, including site conditions that require mitigation, availability of utilities and roadways, and approvals from regulatory agencies (historic, environmental, and other permitting agencies). Project Schedule must identify major design activities, procurement phase activities and construction phasing sequence with major milestones, and VAMC overlapping activation phase. Identify CPM and Risk Analysis Consultants. Crosscheck CPM schedule with estimating consultant for cost escalation. |  | P | U | U | F
G-4.7 | Aggregate |  | Overall Construction Schedule |  |  |  | Submit Construction Schedule showing more details than Project schedule milestones, including phasing sequence, Long lead items and major trade work etc., required by the VA to validate overall phasing and construction durations, which will be the basis of bid. Also, update overall construction schedule using results of Constructability reviews before final design phase. This overall construction schedule shall only be used for VA review and not to be included as a part of final bid package. |  | P | U | U | F
G-4.8 | Aggregate |  | Detail Design Schedule |  |  |  | Submit Detailed Design CPM Schedule identifying major activities, submissions, and milestones including Bid and Award. Show activities for each primary design discipline. At a minimum, include architectural, structural, mechanical, electrical, fire protection and life safety, plumbing, civil, and physical security. This schedule shall be in cost-loaded CPM format with interrelationships. between activities and shall also be used as a basis for monthly payments to the A/E. Provide schedule in Primavera P6 (preferred) or MS Project. |  | P | U | U | F
G-4.9 | Report |  | Risk Management Plan |  |  |  | Submit risk management plan, identify SMEs and methodology on how to execute the plan. Submit Analysis in a narrative format which shall identify schedule risk areas and recommend actions to mitigate identified risks. | F
G-4.10 | Report |  | Schedule Risk Analysis |  |  |  | Submit Schedule Risk Analysis Report based on CPM for detailed design and anticipated overall construction and activation schedule. |  | P | U | U | F
G-4.11 | Report |  | Project Risk Register |  |  |  | Submit a Project Risk Register that has been approved by VA in a timely manner (monthly or as required by VA PM) covering all impacted disciplines. | P | U | U | U | F
G-5.0 |  | COMMISSIONING |  |  |  |  | A/E must coordinate with the commissioning team for the following deliverables:
G-5.1 | Report | [5 empty] | Provide the Commissioning Plan (Cx Plan) coordinated with AE's Basis of Design (BOD), VA’s Project Requirements, and list of systems, components, and features to be commissioned. Include required documentation and schedule for implementation. See Commissioning Process Manual on the TIL. | P | U | U | U | F
G-5.2 | Report | [5 empty] | Identify commissioning team and team organization. Include team member roles and responsibilities, and lines of communication. | F
G-5.3 | Report | [5 empty] | Submit the updated narrative Basis of Design (BOD) report including Commissioning Agent's (CxA) report of document review and statement indicating how each of the items in the report shall be or has been addressed. | P | U | U | U | F
G-5.4 | Report | [5 empty] | Identify major concerns that could affect operations, maintenance, or testing in the design phase commissioning Issues log with proposed resolution/mitigation. Identify discrepancies between Governmental Project Requirements and design narrative. Update design schedule and key milestones and roster of Commissioning Team members. At final submission verify that discrepancies between OPR and design narrative have been resolved. |  | P | U | U | F
G-5.5 | Report | [5 empty] | Provide a Construction and Post-Construction Phase Commissioning Plan, including systems to be commissioned, an outline of construction phase roles and responsibilities, and an outline of required system documentation requirements. |  |  | P | U | F
G-5.6 | Report | [5 empty] | Provide a report on selected control system types, configuration, and capabilities together with key decisions about equipment and systems sequences of operation. |  |  | P | U | F
G-5.7 | Report | [5 empty] | Review technical sections of the specifications to coordinate O&M manual requirements. |  |  |  | P | F
G-5.8 | Report | [5 empty] | Provide description of appropriate training and demonstration requirements for VA’s personnel. Include complete list of all types of equipment/systems and what Training and Demonstration is required. |  |  |  | P | F
G-5.9 | Report | [5 empty] | Submit an updated Basis of Design (BOD) including Commissioning Agent's (CxA) report of document review and statement indicating how each of the items in the report shall be or has been addressed. | P | U | U | U | F
G-5.10 | Report | [5 empty] | Provide a design phase commissioning issues Log with proposed resolution/mitigation. Identify major concerns that could affect operations, maintenance, or testing. Identify discrepancies between Owners Project Requirements and design narrative. Update design schedule and key milestones and roster of Commissioning Team members. At final submission verify that discrepancies between OPR and Design Narrative have been resolved. |  | P | U | U | F
G-5.11 | Report | [5 empty] | Provide description of appropriate training and demonstration requirements for Government personnel. Include complete list of all types of equipment/systems and what Training and Demonstration is required. |  |  |  | P | F
G-5.12 | Report | [5 empty] | Provide preliminary commissioning schedule, inclusive of design phase commissioning schedule and duration schedule for commissioning activities during construction phase commissioning. | P | U | U | U | F
G-5.13 | Report | [5 empty] | For phased construction, coordinate with AE and owner representatives to identify all commissioning requirements within each phase, including required temporary systems. |  | P | U | U | F
G-5-14 | Report | [5 empty] | Provide Commissioning specifications. See Commissioning specifications on the TIL. |  | P | U | U | F
G-5-15 | Report | [5 empty] | Coordinate with AE and owner representatives and identify ALL third party testing. Incorporate third party testing in the Cx Plan and identify all required participants during testing. |  | P | U | U | F
VA SMEs
| Michael Koch |  |  |  |  | Michael.Koch3@va.gov | General
| Elizabeth Yo |  |  |  |  | Elizabeth.Yo@va.gov | BIM
| Ron Johnson |  |  |  |  | Ronald.D.Johnson@va.gov | Specifications
| Mo Ghorbanpour |  |  |  |  | Mo.Ghorbanpour@va.gov | CPM
| Dave Tash |  |  |  |  | Davood.Tashakkori@va.gov | Cx

## Civil
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME |  |  |  |  | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 |  |  |  |  | 0 | 2020-11-01
Seq. No. | Type | Topic |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | CIVIL |  |  |  | VA submission requirements for Civil Design
C-1.0 |  |  | BASIS OF DESIGN
C-1.1 | Report |  |  | Project Survey Marker |  | Verify if a permanent, physical geographic marker in the State Plane Coordinate system/USGS is available on the project campus or site. If not, the Civil Engineer, or licensed surveyor, will establish the Survey Marker to be used for accurately locating buildings, site work, utilities, and infrastructure. The Civil Engineer must provide the coordinate points to the AE for reference before Concept modeling begins, so that BIM can be tied to an accurate survey reference point. | F
C-1.2 | Report |  |  | Site Analysis |  | Review the Project Book analysis for site conditions and identify additional conditions or constraints that need to be addressed. | F
C-1.3 | Report |  |  | Phasing |  | Using the preferred conceptual plan, review the site conditions that will influence project schedule and construction, taking into account existing utility capacity, roadways, approvals from regulatory agencies, etc. |  | P | F
C-1.4 | Report |  |  | Phasing Impacts |  | Phasing analysis to determine impacts of project construction on maintaining hospital routine, ingress/egress of pedestrians and traffic flows, transportation and storage of construction materials, mitigation of air and noise pollution, sequencing of new conflicts, and areas of future construction. | P | U | U | F
C-1.5 | Report |  |  | Erosion Control/ Stormwater Management |  | Sediment and erosion control requirements. |  | F
C-1.6 | Aggregate |  |  | Drainage Analysis |  | Conduct a drainage analysis and provide calculations of existing and proposed site conditions to assess potential options for storm water management strategies. Locate areas where storm water storage facilities are to be located , if needed. |  | P | F
C-1.7 | Calculations |  |  |  |  | Provide storm water computations and sizing calculations to comply with local, state, and federal regulations. Indicate methodology or software used. |  | P | F
C-1.8 | Report |  |  |  |  | Stormwater management requirements and intended methods of implementation. Coordinate with Landscape Architect. Prepare a Storm Water Pollution Prevention Plan (SWPPP) report. Submit SWPPP, required drawings, and calculations to regulatory review agencies, if applicable, as well as VA. |  | P | F
C-2.0 |  |  |  | Geotech
C-2.1 | Report |  |  |  |  | Provide criteria and proposed boring locations plan for a subsurface investigation program to be used for road, parking, and other paving design, where applicable. Proposed boring locations shall be coordinated with boring program for buildings. Conduct percolation test to check soil condition for storm water management. Coordinate with Structural Engineer discipline. |  | P | F
C-2.2 | Report |  |  |  |  | Provide the coordinates (northing, easting, elevation) of each boring or survey line. Boring logs shall include soil descriptions, blow counts, and all other relevant information. Refusal and its relation to top of rock shall be carefully explained and correlated to seismic refraction survey if performed. Geophysical testing and evaluation shall be included where appropriate. Coordinate with Structural Engineer discipline. |  |  | F
C-2.3 | Report |  |  | Geotech Report |  | Using the final Geotech report information, the civil engineer shall create a BIM that reflects the subsurface conditions of the project. Coordinate with Structural Engineer discipline. |  |  | F
C-2.4 | Report |  |  | Narrative |  | Submit Basis of Design narrative for site access, vehicular circulation, physical security standoffs, barriers, parking, and other security elements; and items of environmental and historical significance. |  | P | U | F
C-2.5 | Report |  |  |  |  | Provide a narrative describing infrastructure included to support alternative transportation (mass transit, pedestrian, bicycle, electric vehicle, and etc.) Coordinate with architectural discipline. |  |  | P | F
C-2.6 | Report |  |  |  |  | Emergency Access strategy coordinate with municipalities (fire marshal). |  | F
C-2.7 | Report |  |  |  |  | Mitigation plan (NEPA) |  | F
C-2.8 | Report |  |  |  |  | Site lighting Strategy |  | F
C-2.9 | Report |  |  |  |  | Assess Crime Prevention concepts through Environmental Design (CPTED) principles. | P | U | F
C-2.10 | Report |  |  | Catalog Cut Sheets |  | Provide catalog cut sheets for Site Design related items. |  |  | P | F
C-3.0 |  |  | DRAWINGS and MODELS |  |  | As per the VA BIM STANDARD and as noted below
C-3.1 | Drawings |  |  | Phasing |  | Overall Site Phasing plan. |  |  | P | F | R
C-3.2 | Drawings |  |  | Circulation Plan |  | Circulation plan showing ingress/egress to the site by pedestrians (including persons with disabilities), cars, trucks, emergency vehicles, and mass transit traffic. |  | P | U | F
C-3.3 | [5 empty] | Provide meeting minutes with Fire Marshall. |  |  | F
C-3.4 | Drawings |  |  |  |  | Provide Fire Marshall approved Life Safety plan; indicate fire department access /Roads/ Turnarounds. |  |  | F
C-3.5 | Drawings |  |  | Site Plan |  | Layout plan showing locations of buildings, inlets, equipment at grade, and landscape features. Include dimensioning of parking lots, service courts, and other major elements of the site design. Indicate proposed contractor’s staging area. |  | P | U | U | F
C-3.6 | Drawings |  |  |  |  | Site security diagram indicating all of the physical security elements being implemented into the site design including standoff distances, barriers, access control, and vehicle stacking, at minimum scale 1”=100.0’ (1:1200). Coordinate with Physical Security Requirements. |  | P | U | U | F
C-3.7 | Drawings |  |  |  |  | Provide soil boring locations coordinated with existing utility lines. (coordinate with Structural and Geotechnical. Engineer |  | P | F
C-3.8 | Drawings |  |  |  |  | Provide stormwater management plans/drawings. |  | P | U | U | F
C-3.9 | Drawings |  |  |  |  | Provide site plans including demolition, locations of structures, parking, roads, service areas, walks, plazas, buffers/tree groupings, landscape screening, and other site/building features. Indicate locations of accessible parking spaces and number of handicapped accessible and van accessible parking spaces on site plan. |  | P | U | U | F
C-3.10 | Drawings |  |  |  |  | Provide site plan details, including: fence construction details; guard station and vehicle barrier design; location of cameras, access control and screening equipment; site lighting; vehicle barrier design; landscaping; CPTED implementation plan. |  | P | U | U | F
C-3.11 | Drawings |  |  |  |  | Provide vertical profile(s) and horizontal alignment for roads. Indicate all traversed utilities. |  |  | P | U | F
C-3.12 | Drawings |  |  |  |  | Provide plans for concrete paving joint patterns. |  |  |  | P | F
C-3.13 | Drawings |  |  | Grading |  | Show erosion control and drainage, storm water pollution prevention plan, staging areas, construction access and parking, and stockpile areas for earth and materials. |  | P | U | U | F
C-3.14 | Drawings |  |  |  |  | Provide conceptual grading plan for cut and fill analysis for each proposed concept. | F
C-3.15 | Drawings |  |  |  |  | Grading plan including existing and proposed contours at 2-foot intervals of the entire area affected by the site work. Show spot elevations at structure corners, entrances, equipment pads, other critical areas, and floor elevations for all floors with direct access to grade. Show rim and invert elevations on all storm drainage structures. |  | P | U | U | F
C-3.16 | Drawings |  |  |  |  | Show demolition, erosion, sediment control, and storm water management measures. If rock excavation is required for site grading, indicate quantity on grading plans. |  |  | P | U | F
C-3.17 | Drawings |  |  | Landscape |  | Provide planting plan, with symbols showing location of all trees, shrubs, planting beds, and lawns. Provide a planting list and planting details with botanical and common name, genus and species, size/caliper, and special comments at a minimum. Check plants for suitability to the microclimate, maintenance, safety to patients, and availability. Indicate any areas to be irrigated as per guidance in VA Sustainable Design Manual. |  | P | U | U | F
C-3.18 | Drawings |  |  | Utilities |  | Provide overall utility plan showing all new and existing utilities (storm drainage, sanitary sewer, water, fire (including valves), gas, electric, communications, steam, chilled water, etc.) from building connections to mains. Indicate water storage, fire hydrants and fire department connections. Coordinate with other disciplines to avoid conflicts. |  | P | U | U | F
C-3.19 | Drawings |  |  |  |  | Indicate fire protection items; underground fire main piping and valves, water storage tanks, fire hydrants, fire department connections. |  | P | U | U | F
C-3.20 | Drawings |  |  |  |  | Provide utility drawing showing incoming and outgoing with connections to mains for gas storage (oxygen, nitrogen, and propane) and protection for fuel and water storage. |  | P | U | U | F
VA SME
| James Symanski |  |  |  | James.Symanski@va.gov

## Structural
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 | [5 empty] | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD |  | Pending | N/A | Comments / Location
|  | STRUCTURAL |  |  |  |  | VA submission requirements for Structural Design
S-1.0 |  |  | BASIS OF DESIGN
S-1.1 | Report |  |  | Narrative |  |  | Provide comparative study, with details, supporting calculations and cost estimates, of at least three basic structural systems for typical buildings or wings, as deemed appropriate. Provide written description of the recommended basic structural system, based on the comparative study. Provide written descriptions of the basic structural systems to be used for foundations, substructure, superstructure, provisions for progressive collapse, and lateral force resisting system. Include a short description of other options that were investigated for each system and why they were not chosen. For renovation/addition projects describe existing structural system and strategies for extending, modifying, enhancing the system. Discuss/show whether or not existing structural system meets code provisions that preclude upgrading the existing structural system to meet current code. Provide enough detail for review and cost estimating purposes. |  | P | U | F
S-1.2 | Report | [5 empty] | Provide recommendations for foundation system and, where necessary, mitigation of groundwater penetration. Include discussion of unknown conditions and potential risks involved in preliminary assumptions or site conditions that may impact construction costs. |  | P | U | F
S-1.3 | Report | [5 empty] | Highlight design elements/requirements that are atypical and have potential cost impact. Examples include enhanced detailing for seismic or progressive collapse, finish requirements for exposed structural elements, materials with special properties (high strength, corrosion resistance, etc.). Provide illustrative examples or standard references for these elements and indicate quantities or describe locations where they are to be used. |  | P | U | F
S-1.4 | Report |  |  | Geotech Investigations |  |  | Submit plan to perform subsurface exploration and laboratory testing in the area of any proposed construction. Explain technical issues to be resolved, field and laboratory methods to be used, estimated number and depths of borings and other field methods, estimated laboratory testing, and reporting methods. |  | P | F
S-1.5 | Report | [5 empty] | Indicate whether special geotechnical investigation procedures, e.g. Shear Wave Velocity Measurements and/or Site Specific Study, need to be required for the determination of the more accurate Site Class required to assign Seismic Design Category. Coordinate with Geotechnical / Civil Engineer. |  | P | F
S-1.6 | Report | [5 empty] | Provide two copies of the final geotechnical report. Investigation methods shall be tailored to the needs of the specific project. | F
S-1.7 | Report | [5 empty] | Ground water conditions shall be investigated for each building, including significant excavations greater than 15 feet. This shall include the installation and monitoring of observation wells. When required, monitoring shall continue for at least six months to give an indication of seasonal fluctuation. |  | P | F
S-1.8 | Report | [5 empty] | Provide detailed work plan, which shall include the results of previous investigations relevant to the project. |  | F
S-1.9 | Report | [5 empty] | The final geotechnical report shall include resolution of all comments. Investigation methods shall be tailored to the needs of the specific project. |  |  | F
S-1.10 | Report |  |  | Blast Load Analysis and Design |  |  | Blast Basis of Design (BOD) shall provide analysis and design recommendations for building façade and screen elements including curtain walls and windows, and their connections to the supporting structural elements. These design recommendations shall be developed by close coordination between the Blast Consultant and the Structural Engineer of Record to include locations of connections of building facade elements to supporting structure along with the required connection capacities with some “vendor tolerance factor” accounting for some differences between supplier products. The contractor’s delegated design curtain wall system shall not exceed these specified maximum reactions. |  |  | P | U | F
S-2.0 |  |  | CODE ANALYSIS
S-2.1 | Report | [5 empty] | Using the Project Book code analysis as a basis, do a final due-diligence code analysis for applicable National Codes, VA design criteria and national standards for the project. Note any substantive changes that affect cost. | P | F
S-2.2 | Report | [5 empty] | Describe the Building Structural Performance Design Criteria. |  | F
S-2.3 | Report | [5 empty] | Provide written description of design philosophy for the design of progressive collapse, blast, and natural disaster. |  |  | P | F
S-2.4 | Report | [5 empty] | Identify pre-fabricated structural items (such as pre-engineered metal buildings, precast concrete panels) and other items (Such as building facades, screens etc., that are to be protected against blast loadings)where design is delegated to others. Address design responsibilities related to the designer of record and portions of the design that is being delegated to others. |  |  | P | U | F
S-2.5 | Report | [5 empty] | State the fire resistance criteria for all portions of the structural system. |  |  | P | U | F
S-2.6 | Report | [5 empty] | In close coordination with the mechanical and electrical disciplines, identify equipment that are required to have Special Seismic Certification in accordance with VA criteria. Please see VA H 18-8, Seismic Design Requirements, for a "List of Equipment and Components Typically Requiring Special Seismic Certification" for guidance. |  |  | P | U | F
S-3.0 |  |  | STRUCTURAL TYPE
S-3.1 | Report |  |  | Concrete |  |  | Describe basic material properties for concrete to be used, including compressive strength, entrained air content, maximum aggregate size, allowable water/cement ratio, unit weight or aggregate type, and anticipated admixtures. Potential for fly ash or other suitable cement replacement substitution. Concrete mixtures to be used for footings, foundations walls, slab on grade, elevated slabs, superstructure columns and beams, roof slabs. For rebar, identify bar and welded wire fabric. ASTM material designation for the rebar to be used. Indicate the anticipated uses and locations for special rebar types (epoxy coated, galvanized, and high strength). Determine floor flatness requirements. |  |  | P | U | F
S-3.2 | Report |  |  | Structural Steel |  |  | Indicate ASTM material designation for the steel to be used for each of the following items: steel columns, steel beams, base plates, built-up beams or girders, steel truss chord members, and lateral bracing system. Itemize by American Institute of Steel Construction (AISC) shape as applicable, including material types and sizes. Provide diameter, ASTM material designation, and finish for the typical bolt assembly, including nuts, washers, and bolts. List of the locations where slip-critical bolts are anticipated. Submit the test method to be used to verify the bolt tension in the slip-critical connections. List project welding materials. Provide type of base plate/anchor rod assemblies. Priming/painting of steel members including materials, locations, and slip coefficients. |  |  | P | U | F
S-3.3 | Report |  |  |  | Steel Deck |  | Provide basic information on the anticipated steel decking to be used, including profile and depth, ASTM material designation, span condition, finishes and coatings, and method of attachment. Define required shoring. Deflection criteria to be considered. |  |  | P | U | F
S-3.4 | Report |  |  | Masonry |  |  | Indicate ASTM International (ASTM) designations for typical Concrete Masonry Units (CMU), types of mortar, and lintel materials, ties, and anchors to be used. Define masonry tolerances. |  |  | P | U | F
S-3.5 | Report |  |  | Wood and Engineered Wood Products |  |  | Indicate grade and species for all anticipated wood framing products. Engineering design requirements for engineered wood products. Define typical spacing for framing members. Define special treatment requirements (such as pressure treated and fire resistive). Requirements for wood sheet goods (oriented strand board (OSB), plywood), thicknesses, and locations for use (roof deck, floor deck, exterior sheathing). |  |  | P | U | F
S-4.0 |  |  | REPORTS
S-4.1 | Calculations |  |  | Structural Analysis |  |  | Submit calculations covering all parts of the structure and miscellaneous facilities. Provide copies of input data and output summaries, accompanied by diagrams that identify joints, members, and areas, according to the notations used in the data listings. Calculations shall include: |  |  | P | U | F
S-4.2 | Calculations | [5 empty] | Gravity load and lateral loads for the majority of the framing members |  |  | P | U | F
S-4.3 | Calculations | [5 empty] | Foundations |  |  | P | U | F
S-4.4 | Calculations | [5 empty] | Primary structural members |  |  | P | U | F
S-4.5 | Calculations | [5 empty] | Vibrations |  |  | P | U | F
S-4.6 | Calculations | [5 empty] | Seismic |  |  | P | U | F
S-4.7 | Calculations | [5 empty] | Progressive collapse, local conditions, and blast design.
S-4.8 | Calculations | [5 empty] | Adequacy of existing structure, where applicable, to account for new functional loads or new criteria. |  |  | P | U | F
S-4.9 | Calculations |  |  | Quantities |  |  | General Quantities of structural materials in lb./SF for Cost estimating. |  |  | P | F
S-4.10 | Calculations |  |  | Calculation Sheets |  |  | Final calculations shall be indexed, sealed, and signed by the engineer whose name appears on the Design Calculations index. Observe the following guidelines: |  |  |  |  | F
S-4.11 | Calculations | [5 empty] | State assumptions and design criteria prior to the presentation of the calculations. |  |  | P | U | F
S-4.12 | Calculations | [5 empty] | Provide calculations to verify sizes, bolts, and welds with all details. Connection design may be provided by steel fabricator's engineer in regions where this is standard practice. Refer to AISC Code of Standard Practice requirements for connection information to be shown on documents where design is delegated. |  |  |  | P | F
S-4.13 | Calculations | [5 empty] | Sketches used to describe the basis of calculations shall be drawn to approximate proportions. |  |  |  | P | F
S-5.0 | Drawings |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and as noted below
S-5.1 | Drawings | [5 empty] | Provide drawings of the preferred structural system at the smallest scale that can clearly illustrate the concept ((minimum 1/16” =1’0” (1:200) for larger buildings and 1/8”=1’-0” (1:100) for smaller buildings)). The A/E and VA PM need to concur on drawing scale for the submission. |  | P | F
S-5.2 | Drawings | [5 empty] | Indicate foundation system including walls, footing, and pile locations. |  | P | F
S-5.3 | Drawings | [5 empty] | Indicate floor and roof framing system, including column, beam, and girder locations. Indicate lateral bracing system on the layout. |  | P | F
S-5.4 | Drawings |  |  | General |  |  | Submit the following at a minimum of 1/8” = 1’0” (3.1750 mm) scale drawings showing the selected structural systems, typical details showing relationship of structure with architectural and mechanical features, new and existing construction features, general notes, abbreviations, legends, key notes, symbol keys, key plans, column lines, north arrow, and coordinated backgrounds as per Drawing Deliverable Requirements (DDR). |  | P | U | U | F
S-5.5 | Drawings |  |  | Deep Foundation
S-5.6 | Drawings | [5 empty] | Indicate number, cap size, and size of deep foundation members (pile, pier or caisson) at each location. Indicate the design depth (tip or bottom of elevation) for bidding purposes. |  |  | P | F
S-5.7 | Drawings | [5 empty] | Indicate final number and size of deep foundation members at each location. Indicate the design depth (tip or bottom of pile, pier or caisson elevation) of each deep foundation member for bidding purposes. |  |  | P | F
S-5.8 | Drawings | [5 empty] | Locate test pile, pier, or caisson locations where uplift resistance is critical and geotechnical engineer wants verification of performance. |  |  | P | F
S-5.9 | Drawings | [5 empty] | Indicate completed pile, pier or caisson cap schedule including top of cap elevations, reinforcing, and anchorage. |  |  |  | P | F
S-5.10 | Drawings | [5 empty] | Provide tie-beam information including size, reinforcing, clearances and connection details to pile, pier or caisson caps. |  |  |  | P | F
S-5.11 | Drawings |  |  | Foundation System |  |  | Indicate on the foundation plans the following:
S-5.12 | Drawings | [5 empty] | Wall and slab-on-grade thickness |  |  | P | U | F
S-5.13 | Drawings | [5 empty] | Brick shelf locations |  |  | P | U | F
S-5.14 | Drawings | [5 empty] | Slab-on-grade construction |  |  |  | P | F
S-5.15 | Drawings | [5 empty] | Footing steps and elevator pits |  |  |  | P | F
S-5.16 | Drawings | [5 empty] | Waterproofing and water stop systems; coordinate as shown on the architectural drawings |  |  |  | P | F
S-5.17 | Drawings | [5 empty] | Provide footing schedule on drawings. |  |  | P | U | F
S-5.18 | Drawings |  |  | Expansion Joints |  |  | All building expansion joints. Show foundation wall and slab-on-grade construction and control joints. |  |  | P | F
S-5.19 | Drawings |  |  | Concrete Foundation/Framing Drawings |  |  | Concrete superstructure showing beams, columns, piers, and elevated slabs with locations and sizes/thicknesses, and reinforcing. |  |  | P | U | F
S-5.20 | Drawings |  |  |  | Typical Details |  | Typical details for concrete footings, beams, columns, slabs, and walls as required for the project; Include only details that apply to the scope of work. |  |  | P | U | F
S-5.21 | Drawings |  |  |  | Slab |  | Completed concrete column, beam, pilaster, and footing schedules. Indicate information for concrete slab construction including: |  |  | P | U | F
S-5.22 | Drawings | [5 empty] | Slab joint pattern for concrete slabs-on-grade. |  |  | P | U | F
S-5.23 | Drawings | [5 empty] | Slab thickness and top of slab elevations. |  |  | P | F
S-5.24 | Drawings | [5 empty] | Slab reinforcing including sizes, spacing, placement, and clearances. |  |  | P | U | F
S-5.25 | Drawings | [5 empty] | Typical slab construction details, including construction and control joint details, typical details at slab-column isolation joints, slab-wall joint details. |  |  | P | U | F
S-5.26 | Drawings | [5 empty] | Indicate all changes in slab elevations, including depressions and pits, and sump pits at the bottom of all elevator pits. |  |  |  | P | F
S-5.27 | Drawings | [5 empty] | Indicate all sloped slab locations with both beginning and ending slope elevations. |  |  |  | P | F
S-5.28 | Drawings |  |  |  | Continuous and Isolated Footings |  | Footing sizes, locations, and top of footing elevations. |  |  | P | U | F
S-5.29 | Drawings | [5 empty] | Footing reinforcing sizes, spacing, and clearances. |  |  | P | U | F
S-5.30 | Drawings | [5 empty] | Required keyways and dowels. |  |  | P | U | F
S-5.31 | Drawings |  |  |  | Foundation Walls |  | Elevation at top of wall. |  |  |  | P | F
S-5.32 | Drawings | [5 empty] | Elevation at top of brick shelf or other supports. |  |  |  | P | F
S-5.33 | Drawings | [5 empty] | Elevation at beam pockets and changes in wall heights. |  |  |  | P | F
S-5.34 | Drawings | [5 empty] | Dimension of wall thickness and dimension to column lines. |  |  |  | P | F
S-5.35 | Drawings | [5 empty] | Wall reinforcing size, direction, spacing, and clearances. |  |  |  | P | F
S-5.36 | Drawings | [5 empty] | Integral pier or pilaster size, location, reinforcing, and elevation. |  |  |  | P | F
S-5.37 | Drawings | [5 empty] | Wall penetrations including size, locations, and additional reinforcing. |  |  |  | P | F
S-5.38 | Drawings | [5 empty] | Locations and details for embedded items such as connection plates or anchors. |  |  |  | P | F
S-5.39 | Drawings | [5 empty] | Coordinate and indicate waterproofing and water stop systems shown on the architectural drawings. |  |  |  | P | F
S-5.40 | Drawings |  |  | Structural Steel Superstructure |  |  | All columns and beams. |  |  | P | U | F
S-5.41 | Drawings | [5 empty] | Column sizes and orientation. |  |  | P | U | F
S-5.42 | Drawings | [5 empty] | Beam sizes. |  |  | P | P | F
S-5.43 | Drawings | [5 empty] | Lateral bracing system. |  |  | P | U | F
S-5.44 | Drawings | [5 empty] | Connection moments, vertical, and lateral loads. Detailed design may be provided by steel fabricator's engineer in regions where this is standard practice. Refer to AISC Code of Standard Practice requirements for connection information to be shown on documents where design is delegated. |  |  | P | U | F
S-5.45 | Drawings | [5 empty] | Column schedule. |  |  |  | P | F
S-5.46 | Drawings | [5 empty] | Base plates, anchor bolts, rods, hardware, and pattern. |  |  |  | P | F
S-5.47 | Drawings | [5 empty] | Steel beam camber. |  |  |  | P | F
S-5.48 | Drawings | [5 empty] | Shear stud type and length. |  |  |  | P | F
S-5.49 | Drawings | [5 empty] | Approximate locations and support for major mechanical equipment. Identify and label equipment and weights over 1,000 lbs. on MEP drawings. |  |  |  | P | F
S-5.50 | Drawings |  |  | Steel Faming Drawings |  |  | Steel framing member sizes. Include all shear stud and camber information for floor framing members. |  |  |  | P | F
S-5.51 | Drawings | [5 empty] | Connection design loads including vertical reactions and design moments for moment connections Detailed design may be provided by steel fabricator's engineer in regions where this is standard practice. Refer to AISC Code of Standard Practice requirements for connection information to be shown on documents where design is delegated. |  |  |  | P | F
S-5.52 | Drawings | [5 empty] | Column orientation on framing plans. |  |  |  | P | F
S-5.53 | Drawings | [5 empty] | Locations requiring the installation of slip-critical bolts. |  |  |  | P | F
S-5.54 | Drawings | [5 empty] | Bridging and bracing member sizes, locations, and connections. |  |  |  | P | F
S-5.55 | Drawings | [5 empty] | Metal decking sizes, span criteria, and direction. |  |  |  | P | F
S-5.56 | Drawings | [5 empty] | Relevant typical details. Include only details that apply to the project. |  |  |  | P | F
S-5.57 | Drawings | [5 empty] | Complete column schedule, including member sizes, splice locations and types, base plate sizes and orientation, and column loads and heights. |  |  |  | P | F
S-5.58 | Drawings | [5 empty] | Non-typical or non-standard connection details. |  |  |  | P | F
S-5.59 | Drawings | [5 empty] | Lintels (loose and attached) and support angles. |  |  |  | P | F
S-5.60 | Drawings |  |  | Elevated Slab-On-Deck |  |  | Slab thickness and typical reinforcing. |  |  |  | P | F
S-5.61 | Drawings | [5 empty] | Changes in top-of-slab elevation. |  |  |  | P | F
S-5.62 | Drawings | [5 empty] | Verification that thickness is coordinated with fire-rating requirements. |  |  |  | P | F
S-5.63 | Drawings | [5 empty] | Slab flatness requirements. |  |  |  | P | F
S-5.64 | Drawings |  |  | Masonry Drawings |  |  | Typical masonry reinforcing and spacing requirements for load bearing walls. Assist the architect in reinforcing and spacing requirements for load non-bearing walls shown on architectural drawings. |  |  |  | P | F
S-5.65 | Drawings | [5 empty] | Masonry seismic anchorage and lateral support requirements. |  |  |  | P | F
S-5.66 | Drawings | [5 empty] | Indicate masonry bond beam requirements. |  |  |  | P | F
S-5.67 | Drawings |  |  | Other |  |  | Seismic design. |  |  |  | P | F
S-5.68 | Drawings | [5 empty] | Indicate fireproofing of structural members. |  |  |  | P | F
S-5.69 | Drawings | [5 empty] | Indicate progressive collapse prevention and blast load design (if required). |  |  |  | P | F
VA SME
| Juan Archilla |  |  |  |  | Juan.Archilla@va.gov
| Asok Ghosh |  |  |  |  | Asok.Ghosh@va.gov

## Architectural
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
Combined with USACE MX Supplement
PROJECT NAME | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 | [5 empty] | 0 | 2020-11-01 | [5 empty] | DO NOT AGREE
Submittal Checklist
Seq. No. | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | CD2 (New MX) | Submitted | Pending | N/A | Comments / Location
|  | ARCHITECTURAL |  |  |  |  | VA submission requirements for Architectural Design
A--1.0 |  |  | BASIS OF DESIGN
A-1.1 | Report |  |  | Narrative |  |  | Narrative establishing project goals, and objectives. | P | U | U | U | F
A-1.2 | Report |  |  |  | Quantities |  | Types and quantity of Architectural Significant Equipment (ASE) to be accommodated (linear accelerator, imaging, laundry, food service, etc.). | P | U | U | U | F
A-1.3 | Report |  |  |  | Concept of Operations |  | Update the VA provided Concept of Operations and finalize as the Functional Operations Manual. | U | U | U | U | F
A-1.4 | Report | [5 empty] | Provide functional (medical) and physical design program. | F
A-1.5 | Report | [5 empty] | Provide adjacency matrix for major services. | F
A-1.6 | Report |  |  |  | Code Analysis |  | Coordinate with Fire Protection. Provide a detailed listing of all applicable codes for the project, construction type, design criteria, and national standards affecting the design to ensure that the proposed design complies with applicable regulations, codes, and standards referenced in VA handbooks, design manuals, and standards. Include title, year and publishing organization for each code/standard indicated. Provide description of Structural Design Loading Information (include criteria and reference source.) | P | F
A-1.7 |  |  |  |  | Code Compliance |  | Evaluate and report in the Narratives the proposed design for Code Compliance. | P | U | U | U | F
A-1.8 | Report |  |  |  | Phasing |  | Provide analysis of implementation strategies, phasing, and sequencing considerations. | P | U | U | U | F
A-1.9 | Report |  |  |  | Thermal Envelope |  | Identify and analyze all exterior enclosure elements for compatibility and compliance to energy standards, climatic requirements, and extreme weather events. |  |  | P | U | F
A-1.10 | Report |  |  |  | Construction Alternates |  | Identify/Update potential construction alternates. Deduct alternates shall represent at least 10% of the construction budget. Provide drawings & narrative. Provide cost evaluation for each alternate. Include a rating scale and score sheet for comparison of alteration. |  | P | U | F
A-1.11 | Report |  |  |  | Seismically Restrained |  | Describe seismic constraints needed for casework, equipment, and furniture. |  |  |  | P | F
A-1.12 | Report |  |  |  | Interstitial Study - VAHBS |  | Provide report, analysis, and budgetary impacts to incorporate the VA Hospital Building System (VAHBS) including areas where interstitial space can best be utilized. | P | F
A-1.13 | Report |  |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  | Analyze impact of seismic correction plan on existing functional layout. Determine minimal acceptable changes necessary to implement seismic corrections. | P | U | U | F
A-2.0 |  |  | CONCEPTUAL STUDIES
A-2.1 | Report |  |  | Sustainability, Energy Reduction, Renewable Energy Use |  |  | Identify the Third Party Sustainability rating system (LEED or Green Globes) that will be used. Identify the strategies that show the most promise for this location and building type. | F
A-2.2 | Drawings |  |  | Conceptual Massing and Floor Plans |  |  | Provide (3) 3D-massing concepts, showing departmental adjacencies and major interior and site circulation routes for each concept being developed. Show each department/function and perimeter of each patient room, show each DGSF and total building GSF for each concept. | F
A-2.3 | Report |  |  | Narrative for Concepts |  |  | Use Choosing by Advantages (CBA) to compare concept alternatives for the following: Efficiency of healthcare delivery (departmental adjacencies), interior and exterior circulation/ease of access by patient and services, construction risk, ease of facility management, impact of construction on existing operations, time to First Patient Day, cost of implementation, Physical Security, impact assessment on existing facilities, and project-specific goals. | F
A-3.0 |  |  | SPACE PLANNING
A-3.1 | Report |  |  | Narrative |  |  | Submit a narrative Basis of Design (BOD) report. This must be updated at each design submission showing all previous submission totals and deltas. Highlight all deviations from previous report. Report to include: | P | U | U | U | F
A-3.2 | Report |  |  | Area Summary |  |  | Provide a summary of space comparing the SEPS PFD baseline to the proposed design. The space summaries shall be extracted from BIM. Include room and departmental NSF, conversion factor used, departmental gross (DGSF), and building GSF, highlighting all deltas. Submit in tabular form with subtotal for each room type, department, and common areas such as lobbies, service areas, cafeteria, Mechanical/Electrical equipment, basic circulation, canteen, FMS and OI&T telecommunications, etc. This must be updated at each design submission showing all previous submission totals and deltas. All modifications to the PFD require approval from VA MC, the VA Project Manager, and VACO CFM. | P | U | U | U | F
A-3.3 | Report |  |  | Building Summary |  |  | Summarize building metrics in tabular form: building height, GSF by floor and GSF building total, number of patient rooms, beds by floor, and building occupancy type. | P | U | U | U | F
A-3.4 | Report |  |  | Transportation and Logistics Studies |  |  | Provide a logistics strategy (staging, processing, vertical and horizontal transportation systems, material handling, staffing peaks, travel distances egress). Determine if proposed strategies impact project scope and identify opportunities for sharing services within the facility or with other facilities. Refer to PG 18-3, Topic 18. | P | U | U | F
A-3.5 | Aggregate |  |  | Expansion |  |  | Plan for 25% expansion capability, either vertical or horizontal, to accommodate the Integrated Master Plan for the facility. Include specific departmental direction/requirements for expansion (e.g., emergency, diagnostic imaging, surgery, SPD, etc.) and assure utility connections at the point of expansion are adequate. | P | U | U | F | R
A-3.6 | Aggregate |  |  | BIM Interactive Reviews |  |  | Provide live BIM review of the design, access, and space reservations of major MEPFT equipment/distribution systems. Refer to the VA BIM Manual. Provide a key plan identifying location and direction of rendered view. Provide fit-for-purpose views demonstrating how the design meets functionality requirements. |  |  | P | F
A-3.7 | Aggregate |  |  | Fit for Purpose Design Verification |  |  | Provide design validation as described in the VA BIM STANDARD. |  |  | P | F
A-3.8 | Drawings |  |  | Visually Monitored Spaces |  |  | Provide BIM camera views for Visually Monitored Spaces as noted in the VA BIM STANDARD.
A-3.9 | Drawings |  |  | Communicating the Design Aesthetic |  |  | Provide rendered visualizations as noted in the VA BIM STANDARD. |  | P | U | F
A-3.10 | Drawings |  |  | Swing Space/Design and Construction Phasing Plan (4D) |  |  | Provide a 3D/4D communication plan for swing space and sequence of work. Indicate construction barriers/fences, proposed laydown space and operational logistics. Refer to the VA BIM STANDARD. | P | U | U | U | F
A-4.0 |  |  | ROOM DATA SHEETS |  |  |  | Electronic 2D PDFs (minimum scale 1/4" = 1"-0" (1:50) linked to the plan sets as per the requirements in the DDR. |  |  | P | U | F
A-4.1 | Drawings | [5 empty] | Provide the proposed layouts for complex procedure rooms, patient rooms, typical exam room(s) on enlarged Architectural project-specific floor plans identifying the critical dimensions and equipment for the project that has been exported from SEPS. Room Data Sheets for typical room types include: |  |  | P | U | F
A-4.2 | Drawings | [5 empty] | JSN, Room Codes, and other information as described in the BIM Standards for coding. |  |  | P | U | F
A-4.3 | Drawings | [5 empty] | Minimum room dimensions and clearances. |  |  | P | U | F
A-4.4 | Drawings | [5 empty] | Door size and special requirements (fire rating, vision panel, finish hardware, access control, etc.) |  |  | P | U | F
A-4.5 | Drawings | [5 empty] | Wall types (fire ratings, shielding, acoustic, etc.). |  |  | P | U | F
A-4.6 | Drawings | [5 empty] | Architectural casework configuration and location. |  |  | P | U | F
A-4.7 | Drawings | [5 empty] | Special features such as humidity control, eye wash, lighting. |  |  | P | U | F
A-4.8 | Drawings | [5 empty] | Locker quantities and type. |  |  | P | U | F
A-4.9 | Drawings | [5 empty] | Structural requirements for both room and equipment. |  |  | P | U | F
A-4.10 | Drawings | [5 empty] | Room Finishes. |  | P | U | U | F
A-4.11 | Drawings | [5 empty] | Reflected ceiling plans for project specific rooms, complex and typical. |  |  | P | U | F
A-4.12 | Drawings | [5 empty] | Depict normal, emergency, isolated and UPS requirements. Show lighting, medical gases, plumbing fixtures and controls, data connections, all communication systems (telephone, nurse call, PA, intercom, Wi-Fi). |  |  | P | U | F
A-4.13 | Drawings | [5 empty] | Equipment (fixed and movable) with rough-in requirements; Verify space needs for functional use. Identify equipment by VA Acquisition Code and denote ASE. Coordinate information provided by the equipment planner. Coordinate information provided by the equipment planner, interior designer and food service planner as required. |  |  | P | U | F
A-5.0 |  |  | ARCHITECTURAL DRAWING DELIVERABLES |  |  |  | Follow the requirements in the DDR, the VA BIM STANDARD and as noted below.
A-5.1 | Drawings |  |  | Title/Cover Sheet(s) |  |  | Cover Sheets: project name and address, VA project number, location map, signature block, name and address of VA, architect, engineers, and other consultants; Project Data with index of drawings, legend of abbreviations and symbols; Project Codes and Standards Sheet with a list and summary of the applicable project codes, applicable VA Standard Manuals and Guides by name and issuance date. |  | P | U | U | F
A-5.2 | Drawings |  |  | Site Plans |  |  | Provide a site plan (min. 1"=30.0') indicating demolition, building location, parking, pedestrian and vehicular circulation, emergency vehicle access, loading docks, and all other major landforms and site features. (Coordinate with Civil Engineering discipline). |  | P | U | U | F
A-5.3 | Drawings |  |  | Demolition Plans |  |  | Demolition floor and ceiling plans for areas to be renovated and areas below where work in space below is required (minimum 1/8"=1'-0" (1:100) with finish schedule and wall types. Coordinate with phasing plans, Interim Life Safety Measures (ILSM) and Infection Control Risk Assessment (ICRA). Describe compliance with VA FPDM Section 1.4. |  |  | P | U | F
A-5.4 | Drawings |  |  | Floor Plans |  |  | Provide floor plans showing departmental adjacencies, major circulation routes and layouts for each floor, including interstitial floors, showing internal organization of each department, vertical and horizontal circulation, location of mechanical and electrical equipment rooms, utility shafts, patient and staff entrance, receiving/shipping, and location of section cuts (minimum scale 1/16” =1’-0” (1:200). Included column centerline and overall building dimensions. Coordinate with Civil Engineering discipline for finished floor of structures and flood zones. |  | P | U | U | F
A-5.5 | Drawings | [5 empty] | Provide floor plans identifying room square footages: Net Program / Net Actual. |  | P | U | U | F
A-5.6 | Drawings | [5 empty] | Within each department/function bounding show DGSF actual/program, highlighting all deltas, include FMS and OI&T telecommunications area (combined and separated). |  | P | U | U | F
A-5.7 | Drawings | [5 empty] | Floor plans should identify partition types, sections cuts locations, interior and exterior elevation location, detail locations, large scale plan areas, interior vision panels, millwork, architectural casework, plumbing fixtures, major and fixed equipment. Equipment items must be identified by JSN on other drawings. Indicated proposed future expansion and include interior and exterior dimensions including general notes. Include fire extinguisher and fire hose connection cabinets as applicable. |  |  | P | U | F
A-5.8 | Drawings | [5 empty] | Identify project specific departmental areas for enhanced study thru enlarged plans to be submitted with SD 2. (e.g., surgery, SPS, nursing units, radiology/imaging, & ED). |  | P | F
A-5.9 | Drawings | [5 empty] | Provide 1/8"=1'-0" (3.1750 mm) scale floor plans depicting travel distances from nurse station to patient room(s) and support room to patient room(s), work flow within SPS, surgery & other complex areas. |  | P | U | F
A-5.10 | Drawings | [5 empty] | Delineate on the drawings special conditions such as storage racks/shelving location, height and configuration (including mobile shelving); atria; open ceilings, or architecturally sensitive areas; audiometric booths; walk-in freezers and cold rooms; computer rooms and raised flooring; loading docks and exterior canopies; residential sleeping etc. which may have an impact on sprinkler design and installation. |  | P | U | F
A-5.11 | Drawings |  |  | Accessibility, ABA |  |  | Address compliance with the ABA (Architectural Barriers Act) Accessibility Standard for Federal Facilities, in accordance with VA FPDM Section 1.5. |  | P | U | U | F
A-5.12 | Drawings |  |  | ILSM/ICRA Plans |  |  | Provide Interim Life Safety Measures (ILSM) and Infection Control Risk Assessment (ICRA) drawings at minimum scale 1/16"=1'-0" (1:200). Construction Safety as required showing construction barriers/fences. Describe compliance with VA FPDM Section 1.4. |  |  |  | P | F
A-5.13 | Drawings |  |  | Ceiling Plans |  |  | Reflected ceiling plans (architectural and MEP) at minimum scale 1/8"=1'-0" (1:100). Identify bulkheads, light fixtures, supply and return grilles, ceiling mounted equipment, exit lights, and other devices. Locate ceiling grid. |  |  |  | P | F
A-5.14 | Drawings |  |  | Roof Plans |  |  | Provide 1/8"=1'-0" (1:100) scale roof plans depicting all roof features (drains, overflows, slopes, crickets, ridges, valleys, penetrations, equipment, davits, walk pads, etc.). Indicate all green roof types and areas. |  |  | P | U | F
A-5.15 |  |  |  | Color Coded Departmental Plans |  |  | Submit floor plans color-coded by functional area. |  | P | U | F
A-5.16 | Drawings |  |  | Enlarged Floor Plans |  |  | Provide floor plans at 1/4"=1'-0" (6.3500 mm) scale for all areas. |  |  |  | P | F
A-5.17 | Drawings |  |  | Exterior Elevations |  |  | Provide building elevations at a minimum of 1/16"=1'-0" (1:200) with fenestration, penthouses, materials, finish floor elevations, floor-to-floor heights, overall building height, window and louver types, entrances, canopies, skylights, and adjacent grades. Include separate elevations indicating base building with expansion shown on floor plans. Provide building elevations of complex areas at a minimum scale of 1/4"=1'-0" (1:50). |  | P | U | U | F
A-5.18 | Drawings |  |  | Building Sections |  |  | Provide building sections at minimum scale 1/16"=1'-0" (1:200) through major portions of building. |  | P | U | U | F
A-5.19 | Drawings |  |  | Wall Sections |  |  | Provide wall sections indicating floor-to-floor heights, overall building heights, materials, fenestrations, and assemblies. |  |  |  | P | F
A-5.20 | Drawings |  |  | Wall Types |  |  | Provide each wall type at minimum scale of 1"=1'-0" (1:10). Indicate sound attenuation and fire ratings. Identify UL or other acceptable testing agency design number. |  |  |  | P | F
A-5.21 | Drawings |  |  | Construction Details |  |  | Construction details at scale large enough to clearly show components and assembly: windows, storefront, waterproofing, roof accessories, equipment mounting and suspension shielding, etc. Provide 3D PDF details for all complex roof/wall/window interfaces and include in electronic 2D drawing sets. |  |  |  | P | F
A-5.22 | Drawings |  |  | Vertical Transit Plans & Details |  |  | Vertical transit details for stairs, elevators, lifts, dumbwaiters, linen and trash chutes, and pneumatic tube stations. Provide plans at minimum scale of 1/4"=1'-0" (1:50), sections and details at scale large enough to convey design intent. |  |  |  | P | F
A-5.23 | Drawings |  |  | Door Schedules |  |  | Door schedule with door and frame details, threshold details, door number, door and frame types, dimensions, ratings, materials, glazing, security requirements, and finish hardware. |  |  |  | P | F
A-5.24 | Drawings |  |  | Door Types |  |  | Provide graphical depiction of each door type. |  |  |  | P | F
A-5.25 | Drawings |  |  | Interior Elevations |  |  | Provide interior elevations at minimum scale of 1/4"=1'-0" (1:50) showing medical gases, power, data, communications, millwork, architectural casework, equipment and other built-in items. Identify PRC items by JSN and as noted in the VA BIM STANDARD. |  |  |  | P | F
A-5.26 | Drawings |  |  | Phasing Plans |  |  | Provide plans showing the phasing sequencing considerations etc. |  | P | U | U | F
A-5.27 | Drawings | [5 empty] | Within each department/function bounding show DGSF actual/program, highlighting all deltas, include FMS and OI&T telecommunications area (combined and separated). |  | P | U | F
A-6.0 |  |  | FM Data
A-6.1 | Report |  |  | COBie Format |  |  | Provide FM Data according to VA BIM STANDARD . |  |  |  | P | F
VA SME
| Michael Koch |  |  |  |  | Michael.Koch3@va.gov
| David Treece |  |  |  |  | David.Treece@va.gov

## Medical & Food Equip
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 | [5 empty] | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | MEDICAL EQUIPMENT |  |  |  |  | VA submission requirements for Laboratory/Medical Casework and Food Service
Q-1.0 |  |  | BASIS OF DESIGN
Q-1.1 | Report |  |  | Project Equipment List |  |  | The Project Equipment List includes updated quantities for medical equipment, food service, and FFE from the Space and Equipment Planning System (SEPS) PRC. The Medical Equipment Planner, the Food Service Consultant, and the Interior Designer shall coordinate with the Medical Staff to refine the Project Room Contents (PRC) exported from SEPS. Submit the Project Equipment List in Excel. The Project Equipment List must include all coding in the SEPS BIM Excel Export file listed in the VA Spatial & Equipment Data Spreadsheet and attribute types (e.g., dimensions, cost, etc.) from SEPS with updated quantities. All applicable items requiring utilities are to be coded with a Utility Code as defined in the MIL-STD 1691. Use the SEPS BIM Excel Export file to transfer information for equipment to BIM for room test fits. |  |  | P | F
Q-2.0 |  |  |  | Cut Sheets |  |  | Provide in a digital PDF or 8 1/2"x11" format
Q-2.1 | Report | [5 empty] | Provide cut sheets for all Medical Equipment denoting Acquisition Code (CC, VC, VV). Preliminary submittal to include ASE for SD2. Remainder of equipment to be submitted in subsequent submissions. Coordinate cut sheet submittal with other disciplines as required by the project. |  |  | P | F
Q-3.0 |  |  |  | Meeting Notes
Q-3.1 | Report | [5 empty] | Document meetings and decisions with VHA staff and stakeholders to develop medical equipment lists and plans. | P | U | U | U | F
Q-4.0 |  |  |  | Equipment Plans |  |  | As per the VA BIM STANDARD and below.
Q-4.1 | Drawings | [5 empty] | Provide floor plans at 1/4"=1'-0" (1:50) minimum scale that graphically indicate locations and dimensions of proposed and existing equipment as listed in the Project Equipment List. Equipment plans shall reference the Room Data Sheets for typical rooms, and shall show all unique rooms with equipment layouts. All equipment shall be shown to fit into rooms and be usable. Assign utility codes to equipment as applicable. JSN shall identify all equipment and reference the Project Equipment List, cut sheets, and specifications. Project Equipment Lists shall not be shown on the plans, but shall be included in the specifications. VACO will identify areas during SD2 for over the shoulder reviews of select complex areas and repetitive room types at mid points during the DD phase. |  |  | P | U | F
Q-4/1 | Drawings |  |  |  | ASE |  | Provide floor plans at 1/4"=1'-0" (1:50) minimum scale that graphically indicate all locations for Architecturally Significant Equipment (ASE). Provide a list of rooms and ASE equipment in those rooms for coordination by the Contractor as per the VA BIM STANDARD.
Q-5.0 |  |  |  | Equipment Budget Estimate |  |  | Excel Spreadsheet
Q-5.1 | Report | [5 empty] | Provide an Equipment Budget Estimate categorized by Acquisition Code. |  |  | P | U | F
Q-6.0 |  |  |  | Activation Deliverables Package (Electronic Files) |  |  | All Digital Files provided to the Activation Team in the formats below
Q-6.1 | Report | [5 empty] | Equipment Floor plans at minimum scale of 1/4" - 1'-0" (1:50) with graphic depiction of room locations of ASE: 1) Digital PDF; 2) DWG; 3) Native BIM file format. |  |  |  | F | R
Q-6.2 | Report | [5 empty] | Project Equipment List of all equipment and with separate category for ASE: 1) Digital PDF; 2) Excel; 3) Medical Center Web Based Equipment Program (if applicable). |  |  |  | F
Q-6.3 | Report | [5 empty] | Room Data Sheets: 1) Digital PDF; 2) DWG; 3) Native BIM file format. |  |  |  | F
Q-6.4 | Report | [5 empty] | Equipment Cut Sheets: 1) Digital PDF; 2) PDF. |  |  |  | F
Q-6.5 | Report | [5 empty] | Equipment Budget Estimate: 1) Digital PDF; 2) Excel. |  |  |  | F
|  | FOOD SERVICE EQUIPMENT |  |  |  |  | VA submission requirements for Food Service Equipment
FS-1.0 |  |  | BASIS OF DESIGN
FS-1.1 | Report |  |  | Food Service Equipment List |  |  | Submit the refined Food Service equipment list as part of the Project Equipment List. See Project Equipment List under Medical Equipment. All applicable items requiring utilities are to be coded with a Utility Code as defined in the MIL-STD 1691. |  |  | P | F
FS-2 |  |  |  | Cut Sheets |  |  | Provide in a digital PDF or 8 1/2"x11" format
FS-2.1 | Report | [5 empty] | Provide cut sheets for all Food Service equipment denoting Acquisition Code (CC, VC, VV) and ASE. |  |  | P | F
FS-3.0 |  |  |  | Meeting Notes
FS-3.1 | Report | [5 empty] | Document meetings and decisions with VHA staff and stakeholders to develop Food Service equipment lists and plans. |  |  | P | F
FS-4.0 |  |  |  | Food Service Equipment Plans |  |  | As per VA BIM STANDARD and below:
FS-4.1 | Drawings | [5 empty] | Provide floor plans at 1/4"= 1'-0" (1:50) that graphically indicate locations, dimensions, and ASE of proposed and existing equipment as listed in the Project Equipment List. Food Service Equipment plans shall show all rooms with equipment layouts. All equipment shall be shown to fit into rooms and be usable. Assign utility codes to equipment as applicable. JSN codes shall identify all equipment and reference the Project Equipment List, cut sheets, and specifications. Project Equipment Lists shall not be shown on the plans, but shall be included in the specifications. VACO may require over the shoulder reviews at mid points during the DD phase. Show kitchen hood fire suppression interface to electrical/gas shutdowns as required on MEP Models and drawings. |  |  |  | F | R
FS-5 |  |  |  | Food Service Equipment Budget Estimate |  |  | Excel Spreadsheet
FS-5.1 | Report | [5 empty] | Provide a Food Service Equipment Budget Estimate using Activations software system and categorized by Acquisition Code. |  |  | P | F
FS-6 |  |  |  | Activation Deliverables Package (Electronic Files) |  |  | As per Activations Deliverable Package
FS-6.1 | Report | [5 empty] | Include Food Service in Medical Equipment Activation Deliverables Package |  |  |  | F
VA SME
| Jacob Brown |  |  |  |  | Jacob.J.Brown@va.gov

## Interiors
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 | [5 empty] | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | INTERIOR DESIGN |  |  |  |  | VA submission requirements for Interior Design
ID-1.0 |  |  | BASIS OF DESIGN |  |  |  | Submit the Basis of Design (BOD) report updated at each submittal with the following information:
ID-1.1 | Report |  |  | Narrative |  |  | Provide narrative describing interior design concept, how it meets the needs of the users and the facility, and budget considerations. Discuss appropriateness of material and color selections , how they address patient needs, how they relate to the overall building design, and their appropriateness for the geographical location of the facility. |  | P | F
ID-1.2 | Drawings |  |  | FFE |  |  | Plan FFE based on functional needs and upsize the FFE dimensions to account for changes in FFE final selection at time of procurement and/or installation. Coordinate requirements with VHA and other disciplines as needed. |  | P | F
ID-1.3 | Report |  |  | Inventory Existing Furnishings |  |  | Provide inventory list of existing furnishings planned for re-use. | F
ID-1.4 | Report |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  |  | Analyze impact of seismic correction plan on all interior designs. Determine minimal acceptable changes necessary to implement seismic corrections. |  | P | F
ID-2.0 |  |  | FINISHES |  |  |  | Note all deviations from PG 18-14.
ID-2.1 | Report |  |  | Finish Schedule |  |  | Provide Room Finish Schedule in tabular format that identifies room number (both Design & Wayfinding), materials, and color selections for all exposed surfaces. Identify deviations from PG 18-14 in a separate column. |  |  | P | U | F
ID-2.2 | Report |  |  | Sample Boards |  |  | Provide material and finish sample boards. Provide final colors, finishes, furniture and fabrics, all keyed to floor plans. |  |  | P | F
ID-3.0 |  |  | DRAWINGS |  |  |  | As per the VA BIM STANDARD and below. Min. scale = 1/8" = 1'-0" (1:100)
ID-3.1 | Drawings |  |  | Public Spaces |  |  | Provide fully developed design for major public spaces. Submit elevations, perspectives or other presentations to describe the materials, lighting, and appearance of those spaces. |  |  | P | F
ID-3.2 | Drawings |  |  | Floor Pattern Plans |  |  | Provide patterns for floors. |  |  | P | F | R
ID-3.3 | Drawings |  |  | Legend for Room Finishes |  |  | Legend showing Room Finishes. |  |  | P | U | F
ID-3.4 | Drawings |  |  | Interior Elevations |  |  | Provide interior elevations necessary to convey design intent for finishes and color selections. (See Architectural requirements.) |  |  | P | F | R
ID-3.5 | Drawings |  |  | Architectural Casework |  |  | Coordinate with Architecture. |  |  | P | U | F
ID-3.6 | Drawings |  |  | Millwork and Features |  |  | Coordinate with Architecture. |  |  | P | U | F
|  | FURNISHING, FIXTURES, & EQUIPMENT (FFE) |  |  |  |  | Furniture (moveable), fixed furnishings, non-med equipment,
FFE-1.0 |  |  |  | Room Data Sheets |  |  | Coordinate with Architecture.
FFE-1.1 | Drawings | [5 empty] | Provide FFE information for Room Data Sheets. |  |  | P | F
FFE-2.0 |  |  |  | FFE Cut Sheets |  |  | Provide in a digital PDF and 8 1/2"x11" format
FFE-2.1 | Drawings | [5 empty] | Provide cut sheets for all FFE denoting Acquisition Code (CC, VC, VV). Coordinate cut sheet submittal with other disciplines as required by the project. |  |  |  | P | F
FFE-3.0 |  |  |  | FFE List |  |  | Deliverable: Excel file
FFE-3.1 | Report |  |  |  | Meeting Notes |  | Document meetings and decisions with VHA staff and stakeholders. |  | P | U | F | R
FFE-3.2 | Report | [5 empty] | Refine the SEPS PRC after user meetings with medical staff and incorporate into the Project Equipment List (with all required coding) for all updated Room Contents. Coordinate with Medical Equipment. |  | P | U | F
FFE-4.0 |  |  |  | FFE Plans |  |  | Scale: 1/4" = 1"-0" (1:50)
FFE-4.1 | Drawings | [5 empty] | Provide floor plans that graphically indicate locations of proposed and existing FFE. FFE shall be identified by JSN and referenced in the Project Equipment List, and cut sheets. JSNs may be also be shown on other plan types as required by the project. |  |  |  | F
FFE-5.0 |  |  |  | FFE Budget Estimate |  |  | Submit Budget Estimate at each phase with updated information
FFE-5.1 | Report | [5 empty] | Provide an FFE budget estimate, using SEPS costs and categorized by Acquisition Code. |  | P | U | F
FFE-6.0 |  |  |  | Activation Deliverables Package (Electronic Files) |  |  | All Digital Files provided to the Activation Team in the formats below.
FFE-6.1 | Drawings |  |  |  | Drawings |  | FFE Floor plans: 1) Digital PDF; 2) DWG; 3) Native BIM File format. |  |  |  | P | F
FFE-6.2 | Report |  |  |  | FFE List |  | FFE List: 1) Digital PDF; 2) Excel; 3) Medical Center Web Based Equipment Program (if applicable). |  |  |  | F
FFE-6.3 | Drawings |  |  |  | Room Data Sheets |  | Room Data Sheets: 1) Digital PDF; 2) DWG 3) Native BIM File format. |  |  |  | F
FFE-6.4 | Drawings |  |  |  | FFE Cut Sheets |  | FFE Cut Sheets: 1) Digital PDF |  |  |  | F
FFE-6.5 | Report |  |  |  | FFE Budget Estimate |  | FFE Budget Estimate: 1) Digital PDF; 2) Excel |  |  |  | F
|  | SIGNAGE AND WAYFINDING |  |  |  |  | VA submission requirements for Signage and Wayfinding
SW-1.0 |  |  | BASIS OF DESIGN
SW-1.1 | Report |  |  | Narrative |  |  | Describe wayfinding concept. Adhere to the VA Signage Design Guide. Consider wayfinding needs for the visually impaired (i.e., color, texture, contrast). |  |  | P | U | F
SW-2.0 |  |  | CATALOG CUT SHEETS
SW-2.1 | Report |  |  | Signage Cut sheets |  |  | Provide Signage Cut Sheets depicting: Manufacturer Name, Model No., Dimensions, etc. |  |  |  | P | F
SW-3.0 |  |  | DRAWINGS (Minimum scale = 1/8" = 1'-0" (3.1750 mm)
SW-3.1 | Drawings |  |  | Signage and Wayfinding System |  |  | Submit floor plans and sketches indicating signage finishes, and wayfinding features. Show signage in context with floor and wall patterns, lighting, and other elements. Provide supplemental details at larger scale as necessary to fully describe system. |  |  |  | P | F
SW-4.0 |  |  |  | Site Signage
SW-4.1 | Drawings | [5 empty] | Signage plan and signage schedule, with site locations, construction details, and sign face graphics. |  |  |  | P | F
VA SME
| Orest Burdiak |  |  |  |  | orest.burdiak@va.gov

## Fire Protection
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 | [5 empty] | 0 | 2020-11-01
Submittal Checklist
Seq. No.A11:Q20D69AA11:Q67 | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | FIRE PROTECTION |  |  |  |  | VA submission requirements for Fire Protection Design
F-1.0 |  |  | BASIS OF DESIGN |  |  |  | Submit the Basis of Design (BOD) at each phase with updated information. Report to include:
F-1.1 | Report |  | Narrative |  |  |  | Documentation confirming Project FPE qualifications are met per VA criteria and description for the project and executive summary for key items addressed within the Fire Protection Basis of Design. See the VA Fire Protection Design Manual (VA FPDM) and PG-18-03 Topic 1 for fire protection requirements and other references. |  | P | U | U | F
F-1.2 | Report |  |  | General Code Analysis |  |  | Code analysis that includes height and area limitation evaluation, construction type requirements, and occupancy classifications. Code analysis to assess compliance with NFPA 101 including accessible means of egress for other than healthcare occupancies. Description of building construction type and building separation in accordance with Chapter 2 of the VA Fire Protection Design Manual. The analysis shall reference to NFPA 220 for fire resistive ratings and NFPA 101 for occupancy types per PG-18-03 Topic 1. Coordinate with Architectural Code Analysis. Reference the International Building Code (IBC), depending on occupancy classification, as reference for fire resistance rating for each element of construction. | P | U | U | U | F
F-1.3 | Report |  |  |  | Fire Protection Codes and Standards |  | Listing of all applicable governing and referenced codes either required directly by the VA FPDM or via other codes referenced therein; include editions. | P | U | U | U | F
F-1.4 | Drawings |  |  |  | Fire Protection During Construction |  | See Arch tab under ILSM tasks. |  |  |  | P | F
F-1.5 | Report |  |  |  | Site Considerations |  | Description of fire department access for each facility complying with NFPA 1. Describe overall site accessibility, property lines, public way, clear yard setbacks, fire separation distances between structures, secured access impacting emergency response, on-site hazardous material locations per NFPA 1, and any coordination items necessary for emergency response personnel awareness. Description should include location of fire department connections (FDCs), fire alarm control unit and panels and microphone for two-way communication systems. |  | P | U | U | F
F-1.6 | Report |  |  |  | Existing Systems |  | Description of fire protection features for existing facility. Describe sprinkler system type, hazardous material locations, and any items necessary for emergency response personnel awareness. |  | P | U | U | F
F-1.7 | Report |  |  | Building Features |  |  | Incorporate Building Features as denoted below: |  | P | U | U | F
F-1.8 | Report |  |  |  | Occupancy Classification |  | Identification of space using and occupancy classification in accordance with VA FPDM Chapter 4 and NFPA 101. |  | P | U | U | F
F-1.9 | Report |  |  |  | Special Occupancies/Protection |  | Compliance with specialty occupancies such as, but not limited to, health care, laboratories per NFPA 45, parking structures, high-rises, hazardous materials/processes, underground buildings, combustible storage, IT/communication uses per NFPA 75/76, emergency power systems per NFPA 110/111, and others identified in VA FPDM Chapter 3, NFPA 101 Chapter 11, or NFPA 1. Where applicable to each special use, describe the configuration and address classification, fire resistive construction, fire extinguishing/alarm systems, and any other items necessary to demonstrate compliance. |  | P | U | U | F
F-1.10 | Report |  |  |  |  | Information Technology and Telecommunications | Description of the passive fire protection features and the proposed protection and detection in accordance with the VA FPDM. |  | P | U | U | F
F-1.11 | Report |  |  |  |  | Laboratories | Description of the location within the facility and the proposed fire protection features of laboratories, where provided, in accordance with NFPA 45 including the laboratory classification, fire separations due to occupancy and the quantities of flammable and combustible liquids stored, and standpipe requirements, if any. |  | P | U | U | F
F-1.12 | Report |  |  |  |  | Atrium Smoke Control Systems | Description of the smoke evacuation system required for the atrium in accordance with the VA FPDM. |  | P | U | U | F
F-1.13 | Report |  |  |  |  | VA Hospital Building System (VAHBS) | Description of the fire protection features of the VAHBS where the VAHBS is used in the design in accordance with VA FPDM. |  | P | U | U | F
F-1.14 | Calculations |  |  |  | Type of Construction, Building Height and Area |  | Height and area limitation evaluation, construction type requirements, and building separation, in accordance with VA FPDM Section 2.1 /2.2and NFPA 220. |  | P | U | U | F
F-1.15 | Report |  |  |  | VA Hospital Building System (VAHBS) |  | Description of the fire protection features of the VAHBS where the VAHBS is used in the design in accordance with VA FPDM. |  | P | U | U | F
F-1.16 | Report |  |  |  | Fire Resistive Construction |  | Incorporate Fire Resistive construction as denoted below: |  | P | U | U | F
F-1.17 | Report |  |  |  |  | Structural and Exterior Fire Resistance | Provide basis of design UL assemblies associated with each fire-resistance rated assemblies for structural protection including beams, columns, horizontal assemblies, secondary members; address exterior rated or load bearing wall requirements. Description should indicate materials to be used and fire resistive rating of each construction element. |  | P | U | U | F
F-1.18 | Report |  |  |  |  | Combustible Materials | Description of combustible material requirements of VA FPDM and IBC Section 603. |  | P | U | U | F
F-1.19 | Report |  |  |  |  | Interior Finishes | Description of permitted interior finish requirements based upon occupancy. |  | P | U | U | F
F-1.20 | Report |  |  |  |  | Interior Separations, Openings, and Penetrations | All applicable requirements for any fire-resistive construction used, including assembly ratings, requirements for opening and penetrations, protection of construction joints. Include analysis of the requirements for fire dampers and smoke dampers in reference to NFPA 101 and the corresponding references {i.e., NFPA 90A}. (Do not follow the requirements in the International Building Code (IBC) nor the International Mechanical Code (IMC). |  | P | U | U | F
F-1.21 | Report |  |  |  | Means of Egress |  | Address compliance with VA FPDM and NFPA 101. |  | P | U | U | F
F-1.22 | Report |  |  |  |  | Fire and Smoke Dampers | Analysis of the requirements for fire dampers and smoke dampers in reference to NFPA 101 and the corresponding references {i.e., NFPA 90A}. (Do not follow the requirements in the International Building Code (IBC) nor the International Mechanical Code (IMC). |  | P | U | U | F
F-1.23 | Report |  |  | Water Supply for Fire Protection |  |  | Description of the water supplies, water distribution system layout, sizes and hydrant locations and fire department connections for each building and all operating features as a water distribution and supply network. Include fire hydrant flow test data. |  | P | U | U | F
F-1.24 | Report |  |  |  | Fire Pumps |  | Analysis of the requirements for fire pumps and description and locations of fire pump(s) and drivers based on water supply and demand and electrical power available. |  | P | U | U | F
F-1.25 | Report |  |  | Fire Extinguishing Systems |  |  | Description of type and locations of sprinkler systems and analysis of sprinkler system requirements including estimated demands and the use of air or nitrogen or antifreeze for areas subject to freezing. Description of the proposed zoning of systems in accordance with the VA FPDM. |  | P | U | U | F
F-1.26 | Report |  |  | Fire Alarm Systems |  |  | Description for the type of fire alarm system (general evacuation or defend in place; hardwired or analog addressable; type of notification) in accordance with the VA FPDM Chapter 7. Description of proposed zoning in accordance with the VA FPDM. |  | P | U | U | F
F-1.27 | Report |  |  |  | Smoke, Carbon Monoxide, and Heat Detection |  | Description of the location of any required smoke detection, carbon monoxide detection, and heat detection as required by the VA FPDM and NFPA 101. |  | P | U | U | F
F-1.28 | Report |  |  |  | Off premises connection |  | Description of the connection to the base loop or the campus fire alarm system and the method and means of communication to a remote supervisory station. |  | P | U | U | F
F-1.29 | Report |  |  |  | Interfaces |  | Description of fire alarm system interfaces with other fire protection equipment and building systems including, but not limited to, control valves, sprinkler systems, dry pipe systems, reaction systems, deluge systems, kitchen hood extinguishing systems, clean agent systems, smoke and fire dampers, air handling units (fan shut down), door locks, elevators, tank and room temperature alarms, tank level indicators, fire pumps, and emergency generators. |  | P | U | U | F
F-1.30 | Report |  |  |  |  | Clean Agent Fire Systems | Description of any proposed clean agent extinguishing system including all areas to be protected. |  | P | U | U | F
F-1.31 | Report |  | Catalog Cut Sheets |  |  |  | Provide Fire Protection Devices catalog cut sheets. |  |  | P | U | F
F-1.32 | Report |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  |  | Analyze impact of seismic correction plan on all fire protection systems. Determine minimal acceptable changes necessary to implement seismic corrections. |  | P | U | F
F-2.0 |  |  | CALCULATIONS
F-2.1 | Calculations |  |  | Preliminary |  |  | Submit preliminary or updated calculations at each phase to reflect comments from previous and evolved design. |  |  | P | U | F
F-2.2 | Calculations |  |  | Water Supply Sizing |  |  | Submit calculations to size fire pumps (when required), water supply available/maximum demand, on-site water storage/reservoirs, and water flow testing results raw data. |  |  | P | U | F
F-2.3 | Calculations |  |  | Egress |  |  | Occupant load and egress calculations for each floor that justify the number of exits and egress width provided; show both required and actual. |  |  | P | U | F
F-3.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
F-3.1 | Drawings |  | General Sheets |  |  |  | Provide listing of edited VA standard symbols, abbreviations, and standard details. |  |  | P | U | F
F-3.2 | Drawings |  | Site Fire Protection and Code Plan |  |  |  | Show items described in the narrative: fire department access for each facility complying with NFPA 1, overall site accessibility, property lines, public way, clear yard setbacks, fire separation distances between structures, secured access impacting emergency response, on-site hazardous material locations, and any coordination items necessary for emergency response personnel awareness. Show building perimeter where used for frontage increase, fire department connections, PIV's, fire hydrants, water distribution main/size, water storage tanks, hazardous material locations, fire pump room, backflow prevention devices, main fire alarm control unit and annunciator locations. |  |  | P | U | F
F-3.3 | Drawings |  | Code Analysis Summary |  |  |  | Provide summary of BOD Narrative. |  |  | P | U | F
F-3.4 | Drawings |  | Code Plans |  |  |  | Reference this section (F-3.4) of VA's PG 18-15. Add to those requirements: Recommend including the use of these plans as the Life Safety plans for the initial TJC Statement of Conditions documentation. Change the term 'zone' to 'compartment.’ |  |  | P | U | F
F-3.5 | Drawings | [5 empty] | Indicate room names, room numbers, door locations and swings, smoke- and fire-rated barriers, and sprinkler/standpipe risers to floor plans. |  |  | P | U | F
F-3.6 | Drawings | [5 empty] | Locate fire extinguishers and fire hose cabinets. |  |  |  | P | F
F-3.7 | Drawings | [5 empty] | Indicate fireproofing of structural members where applicable. |  |  | P | U | F
F-3.8 | Drawings | [5 empty] | Locate exit signs and emergency lighting. |  |  |  | P | F
F-3.9 | Drawings |  |  | Fire-Resistance-Rated Construction |  |  | Depict structural fire-resistance requirements and locations based on Type of Construction; additionally, barriers requiring fire resistance rated supporting construction must be specifically identified for coordination with the structural design. Show any occupancy separations, fire walls, fire barriers, smoke barriers, compart mentation, fire area separations, separation from hazards (vertical and horizontal for all, including perimeter curtain wall containment); indicate requirements for vertical openings and horizontal penetrations. Summarize associated opening and penetration ratings for each rated assembly (IE: interior and exterior doors/windows, ductwork, conduit/piping, construction joints, etc.). Indicate any delineation in Interior Finish requirements. |  |  | P | U | F
F-3.10 | Drawings |  |  | Hazardous Locations |  |  | Locate hazardous materials storage, handling and use that exceed the maximum allowable quantities. |  |  | P | U | F
F-3.11 | Drawings |  | Fire Extinguishing Systems |  |  |  | Indicate sprinkler zones at a legible scale that shall show an entire floor per drawing. Where smoke compartments are provided, the sprinkler system shall be zoned and supervised by the fire alarm system by smoke compartment. |  |  | P | U | F
F-3.12 | Drawings | [5 empty] | Indicate room names, room numbers, door locations and swings, smoke- and fire-rated barriers, and sprinkler/standpipe risers to floor plans. Identify psychiatric areas requiring institutional-type heads on the drawings. Refer to equipment or architectural drawings that affect sprinkler design (storage racks, library racks, mobile shelving, etc.), Specific occupiable areas not to be protected by automatic sprinklers. |  |  | P | U | F
F-3.13 | Drawings | [5 empty] | Indicate sprinkler/standpipe risers supply piping; Above ground piping including (do not show sprinkler layout) o Connection to underground supply o Sprinkler mains o Fire department connections o Risers o Standpipes and hose connections o Control valves o Terminations of sprinkler system drains to a safe location (exterior to bldg.) o Water flow, water pressure, and tamper switches o Air and nitrogen system switches |  |  |  | P | F
F-3.14 | Drawings | [5 empty] | Locate terminations of sprinkler main and inspector test drain. |  |  |  | P | F
F-3.15 | Drawings | [5 empty] | Determine sprinkler design hazards per NFPA 13. |  |  |  | P | F
F-3.16 | Drawings | [5 empty] | Provide details of the fire pump system, an enlarged plan of fire pump room, including elevation and detail of fire pump, Rated enclosure (or separation) in accordance with NFPA 20, Accessibility by fire department, Details of the fire pump location, controller, piping, and test header, Details of the jockey pump, Reference electrical drawing for power. Plan shall include all fire pump-related mechanical and electrical equipment and accessories to ensure adequate space provided for installation, operation and maintenance of said equipment. |  |  | P | U | F
F-3.17 | Drawings | [5 empty] | Indicate the kitchen hood fire suppression system; Show interface to electrical/gas shutdowns as required on MEP drawings. |  |  |  | P | F
F-3.18 | Aggregate | [5 empty] | Discuss the use of clean agent systems (if any) • Area to be protected by clean agent system • Location of clean agent supply containers • Passive fire protection features • Clean agent alarm system riser diagram • Clean agent alarm system floor plans showing all devices • All interface locations to be shown including Interface to AHU (by number) for shutdown (reference to HVAC drawings), Door hold-opens, Smoke dampers, Power supplies for panels, Connection to fire alarm system, Abort switches, Emergency power off switches • Input/output matrix and sequence of operation |  |  |  | P | F
F-3.19 | Drawings |  | Fire Alarm Systems |  |  |  | Provide fire alarm, and smoke zones at a legible scale that shall show an entire floor per drawing. Where smoke compartments are provided, the zoning of the fire alarm shall coordinate to coincide with the configuration of the smoke. |  |  | P | U | F
F-3.20 | Drawings | [5 empty] | Indicate fire alarm risers showing new equipment and/or necessary changes if modification to the existing system is required. |  |  |  | P | F
F-3.21 | Drawings | [5 empty] | Provide an input/output matrix; sequence of operations. |  |  |  | P | F
F-3.22 | Drawings | [5 empty] | Define interconnection of HVAC system (dampers, fans) with duct smoke detectors and/or fire alarm system. |  |  |  | P | F
F-3.23 | Drawings | [5 empty] | Determine interface of new and existing fire alarm system. |  |  |  | P | F
F-3.24 | Drawings | [5 empty] | Indicate all interface locations to be shown including: o Interface to AHU (by number) for shutdown (reference to HVAC drawings) o Door hold-opens o Elevator recall and shutdown o Smoke dampers o Kitchen hood suppression systems o Sprinkler flow and tamper switches o Air and nitrogen switches o Fire pumps o Door locking o Clean agent system control unit o Power supplies for panels o Connection to off-premises receiving station o Atrium smoke control |  |  |  | P | F
F-3.25 | Drawings | [5 empty] | Indicate zoning of each fire alarm initiating device. |  |  |  | P | F
F-3.26 | Drawings | [5 empty] | Locate and detail annunciator panel when provided. |  |  |  | P | F
F-3.27 | Drawings | [5 empty] | Coordinate with reference notes on HVAC drawings that indicate interconnection of HVAC system (dampers, fans) with duct smoke detectors and/or fire alarm system. |  |  |  | P | F
VA SME
| Peter Larrimer |  |  |  |  | peter.a.larrimer@va.gov

## Plumbing
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME |  |  |  |  | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 |  |  |  |  | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | PLUMBING |  |  |  | VA submission requirements for Plumbing Design
P-1.0 |  |  | Basis of Design
P-1.1 | Report |  |  | Narrative |  | Plumbing designer shall coordinate with both civil and mechanical engineers to provide descriptions of the proposed utilities for the building: fuel gas, oxygen, and water sources, sewage disposal systems, irrigation, and water services, roof drainage, etc. Provide solutions to water or sewage treatment, pumping, and storage if required. Review Project Book report and note which existing utilities and equipment can be used for this project. |  | P | U | F | R
P-1.2 | Report |  |  | Water Analysis |  | If required in the Project Book water analysis, provide proposed solution for a water softener or special water systems such as reverse-osmosis. Identify acid or chemical resistant piping. |  | P | U | F | R
P-1.3 | Report |  |  | Renewable Solar Energy |  | Explanation and technical backup information as to how the project shall meet the project goal for hot water generation using renewable solar energy. Show Life Cycle Cost Analysis calculations. |  | P | U | F | R
P-1.4 | Report |  |  | Potable Water |  | Determine potable water baseline and required reduction target. Define strategies to achieve the reduction goals. |  | P | U | F | R
P-1.5 | Report |  |  |  |  | Provide a graphical representation of water usage savings with reference to the contributing technologies and their weighted contributions . |  |  | P | F | R
P-1.6 | Report |  |  | Systems Coordination |  | Indicate civil discipline invert elevations at the interface with site utilities including domestic water, solar heated water, sanitary, and storm drainage from roof, etc. |  |  | P | F | R
P-1.7 | Report |  |  | Condensation |  | Provide recommendations for installing insulation on the domestic water and horizontal storm drainage piping. |  |  | P | U | F
P-1.8 | Report |  |  | Utility Companies |  | Coordinate with utility companies, where applicable. Provide written approval of utility availability by utility companies or regulatory review agencies, where applicable. |  | P | U | F | R
P-1.9 | Report |  |  | Catalog Cuts |  | Provide plumbing fixture catalog cuts. |  |  |  | P | F
P-1.10 | Report |  |  | Legionella Control |  | Provide documentation and design compliance with VHA Directive 1061 and the VA Plumbing Design Manual regarding the prevention of Legionella disease and scald injury from potable water distribution systems. |  |  | P | U | F
P-1.11 | Report |  |  | Medical Gasses |  | Address sources/producers, risk categories, and how redundancy, continuity, and reliability requirements are being met. Address the coordination of medical gas terminal outlets and manufactured assemblies as per most current NFPA 99. |  | P | U | U | F
P-1.12 | Report |  |  | Water and Sanitary Sewer |  | Address how domestic water and sanitary sewer redundancy, continuity, and reliability requirements are being met. |  | P | U | U | F
P-1.13 | Report |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  | Analyze impact of seismic correction plan on plumbing and sanitary systems. Determine minimal acceptable changes necessary to implement seismic corrections. |  | P | U | F
P-2.0 |  |  | CALCULATIONS
P-2.1 | Calculations |  |  | Systems and Equipment Sizing |  | Plumbing engineer shall coordinate with other engineer disciplines for systems and equipment sizing where necessary. Show calculations for equipment and pipe sizing. |  | P | U | F | R
P-2.2 | Calculations |  |  | Water Usage |  | Provide potable water baseline and reduced consumption calculations to achieve the VA water consumption reduction goals. |  |  | P | F | R
P-2.3 | Calculations |  |  |  |  | Report on types and number of products that are water-efficient. |  |  | P | F
P-2.4 | Calculations |  |  |  |  | Show how the sewage water from the 96 hour retention tank would drain to sewer lines or lift pump if required. |  |  | P | U | F
P-2.5 | Calculations |  |  | Storm Water Discharge |  | Provide storm water computations, sizing calculations, and site analysis to comply with local, state, and federal regulations. Indicate methodology or software used. |  |  | P | U | F
P-2.6 | Calculations |  |  |  |  | Provide calculations for storm water and sizes of rain leader, overflow pipes, or scuppers. |  |  | P | F | R
P-2.7 | Calculations |  |  | Water Pressure Testing |  | If water pressure measurement is older than 1 year a Fire Protection Engineer must obtain a new fire flow test for water pressure and flow at two fire hydrants serving each building in project indicating depth of cover. |  | F
P-2.8 | Calculations |  |  | Medical Gasses |  | Calculations for medical gasses vacuum system and WGAD system. |  |  | P | U | F
P-2-09 | Calculations |  |  | Soil, waste, and vent |  | Provide calculations for soil, waste and vent system including pipe sizing. Provide calculations of natural gas system and pipe sizing. |  |  | P | U | F
P-3.0 |  |  | DRAWINGS and MODELS |  |  | As per the VA BIM STANDARD and below
P-3.1 | Drawings |  |  | Demolition Plans |  | Provide 1/8” = 1’0” (1:100) scale demolition plumbing floor plans. |  |  | P | U | F
P-3.2 | Drawings |  |  | Utility Plans |  | Provide location, types, and sizes of existing and proposed utilities. Plumbing Designer, Civil Engineer, and Landscape Architect shall collaborate and coordinate plans.Provide location ofexisting and proposed storage facilities (if required) and/or areas of lawn irrigation. Indicate any areas of specialty systems. Existing and proposed underground utilities shall be modeled in BIM (see General Tab). |  |  | P | F | R
P-3.3 | Drawings |  |  | Utilities |  | Plumbing Designer, Architect, Mechanical and Electrical Engineer shall collaborate and coordinate plan(s) for emergency and normal power requirements for: medical gases and systems, plumbing fixtures, water and sanitary storage, distribution, and control systems. |  |  | P | U | F
P-3.4 | Drawings |  |  | Riser Diagrams |  | Provide isometric and flow diagrams of domestic water. |  |  | P | F | R
P-3.5 |  |  |  | Schematic Diagrams |  | Provide single line schematic diagrams of the site distribution and domestic water systems demonstrating how hot & cold water is: distributed, balanced, circulated, isolated by valve, stored, flushed, sampled, heated and cooled, treated, drained, and monitored including temperature. Indicate location of makeup systems, outdoor air intakes, no flow and low flows portions of the piping, possible cross connections between potable and non-potable water system and major building water equipment. Identify any areas in which water is processed differently (e.g., hemodialysis and sterile processing). |  |  | P | U | F
P-3.6 | Drawings |  |  |  |  | Provide line diagrams of medical gasses. |  |  |  | F | R
P-3.7 | Drawings |  |  |  |  | Provide 1/8" = 1'-0" (1:100) scale floor plan drawings and riser diagrams indicating room names, locations of existing and new equipment, and plumbing fixtures using VA fixture numbers and VA BIM Standards Coding requirements. Indicate interface of new systems with existing. Show location of air compressors, vacuum pumps, sewage ejectors, domestic water heaters and main risers, roof drains and overflow, pipe sizes, medical gas cylinders manifolds, and backup water supply. Submit schedules, notes, and legends for equipment and distribution systems on drawings. Examine choke points with other trades and validate floor to floor heights. |  | P | U | F | R
P-3.8 | Drawings |  |  |  |  | Provide location of grease traps and waste recovery systems. |  |  | P | F | R
P-3.9 | [5 empty] | Special systems: Medical gas, R/O water, Dealkalizing System, connections to medical equipment, floor and roof drains, and overflow protection. |  |  | P | U | F
P-3.10 | Drawings |  |  | Sterile Processing Service (SPS) |  | Show a NFPA 99 Level 3 medical air system for Sterile Processing Service (SPS) that is separate from any patient care medical air system. (The use of a medical air system meant for patient care in (SPS) is not permitted under NFPA 99.) |  |  | P | F | R
P-3.11 | Drawings |  |  | New Building Equipment |  | Provide 1/4” = 1’0” (1:50) scale floor plans showing location and sizing of new equipment that services the building. Show clearance requirements. The footprints shown for major plumbing and med gas equipment should be based on actual sizes of equipment from at least 3 manufacturers. Details at appropriate scale. |  | P | U | F | R
P-3.12 | Drawings |  |  | Architecturally Significant Equipment (ASE) |  | Provide 1/4” = 1’0” (1:50) plans showing location and sizing of utility connections to ASE identified equipment. |  |  | P | F | R
VA SME
| Snehal Desai |  |  |  | Snehal.Desai@va.gov

## Mechanical
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAMEAA8:Q29 | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 | [5 empty] | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | HEATING, VENTILATING & AIR CONDITIONING |  |  |  |  | VA submission requirements for Heating, Ventilating & Air Conditioning
M-1.0 |  |  | BASIS OF DESIGN |  |  |  | Submit the Basis of Design (BOD) report updated at each submittal with the following information:
M-1.1 | Report |  |  | Narrative |  |  | Provide a Narrative describing the following:
M-1.2 | Report |  |  |  | Concept Energy & Resource Consumption |  | Provide concept assessments including the existing building energy and resource consumption baseline. (For new buildings, document the existing inventory baseline.) Include investigation of the use of high-efficiency, low-pressure hot water boilers for heating application. | P | U | F
M-1.3 | Report |  |  |  | Energy Saving |  | Discuss alternative ways to meet the increased demand and what type of energy-saving measures will be examined in the Schematic Design phase. Also, describe how will the requirements of energy efficiency and savings codes be met. | P | U | U | F
M-1.4 | Report |  |  |  | Spare Capacity |  | Submit specific recommendations for meeting the HVAC needs of the project including expansion of existing systems and plants. |  | P | F
M-1.5 | Report |  |  |  | Three HVAC System Alternatives |  | Submit an analysis for selecting three different types of HVAC systems, the criteria and rationale for evaluating the three systems, and a life cycle cost analysis for each system. Coordinate with the VA HVAC Design Manual wherein the restrictions on the system type and the capacity limitations are outlined. Coordinate with the architect to determine thermal envelope. | P | F
M-1.6 | Report |  |  |  | Energy Efficiency and Conservation |  | Describe energy efficiency and conservation measures proposed to be used in the HVAC system design and the life cycle cost analysis. Refer to VA guidelines for the mandated energy conservation requirements and energy consumption goals. State the logic and criteria for selecting each conservation measure. Also, perform energy modelling and justify the proposed measures. |  | P | U | F
M-1.7 | Report |  |  |  | HVAC System |  | Provide detailed description of the heating, ventilating, and air conditioning (HVAC) systems and equipment for each functional space. |  | P | U | F
M-1.8 | Report | [5 empty] | Provide determine the mechanical system size, and space requirements. Include redundancy requirements for the systems. |  |  | P | F
M-1.9 | Report |  |  |  | Seismic |  | Description of seismic criteria (if applicable) on the HVAC systems. |  |  | P | F
M-1.10 | Report |  |  |  | Severe Weather Impacts |  | Describe the potential impact of severe weather and climate conditions (hurricanes, ice, snow, flood, humidity, coastal areas, wind borne rain) on the HVAC equipment. |  | P | U | F
M-1.11 | Report |  |  |  | Zones |  | Provide a description of the tentative zoning of the spaces, including those proposed with dedicated HVAC systems. Describe the locations of the equipment serving each zone, focusing on the serviceability and maintainability of each major piece of equipment. |  | P | U | F
M-1.12 | Report |  |  |  | Backup Systems |  | Identify redundant/backup/emergency systems/equipment. |  | P | U | F
M-1.13 | Report |  |  |  | Acoustical Impact |  | Describe acoustical impact of mechanical systems/equipment to stacked or adjacent spaces for both new and existing projects. |  | P | U | U | F
M-1.14 | Report |  |  |  | System Interaction |  | Provide description of the interaction between the existing HVAC systems and the new requirements. State the impact on the existing HVAC systems and the project cost. (Examples include: additional Testing, Adjusting, and Balancing effort, replacement of components, suspended ceiling, painting, and fixtures.) |  | P | U | F
M-1.15 | Report |  |  |  | ECC |  | Analyze the feasibility of using the existing central Engineering Control Center (ECC) for the automatic temperature control requirements of the new project. Address the key issues of the available spare capacity and open-protocol BACnet compatibility. |  | P | U | F
M-1.16 | Report |  |  |  | Operational Sequence |  | Provide description of the mechanical sequences of operation. State that the energy model represents these operational parameters and uses actual equipment performance curves from the design selections (mechanical, plumbing, and lighting). |  |  |  | P | F
M-1.17 | Report |  |  |  | Metering Requirements |  | Provide evidence of coordination of the metering requirements with the ongoing activities at the existing facilities and provide a brief description of the scope of work and extent of coordination involved. Define the work by a single line schematic diagram showing components and the interface between systems. |  | P | U | U | F
M-1.18 | Report |  |  |  | Room Data Sheets |  | Provide evidence of coordination of HVAC requirements on room data sheets (see Architectural requirements). |  |  | P | F
M-1.19 | Report |  |  |  | Coordination |  | Provide evidence of discipline coordination to accommodate all Architecturally Significant Equipment to include, but not limited to: sterilizing equipment, kitchen equipment, automatic cart washer, fume hoods, biological safety cabinets, radiology, and nuclear medicine equipment specified for the project. Present all VA-approved deviations from HVAC design criteria. (Any request for deviation from HVAC design criteria must be approved by VA and occur no later than the design development stage). | P | U | U | U | F
M-1.20 | Report |  |  | Energy Model |  |  | Preliminary Energy Model for Mechanical Systems. See Sustainability Manual for criteria. |  | P | F
M-1.21 | Report | [5 empty] | Submit energy modeling report using operational parameters of all designed systems and uses actual equipment performance curves from the design selections (mechanical, plumbing, and lighting). Discuss any adjustments and their effects from the previous submittal. |  | P | U | F
M-1.22 | Report |  |  | Mechanical Equipment |  |  | Provide complete selection data, including catalog cut sheets for all HVAC equipment. |  |  |  | P | F
M-1.23 | Report |  |  | O&M |  |  | Provide narratives discussing direct access for O&M of major equipment and a practical means of future replacement. |  | P | U | U | F
M-1.24 | Report |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  |  | Analyze impact of seismic correction plan on all heating, ventilating and air conditioning systems. Determine minimal acceptable changes necessary to implement seismic corrections. | P | U | U | F
M-2.0 |  |  | CALCULATIONS
M-2.1 | Calculations |  |  | Selected HVAC System |  |  | Provide an analysis of the selected HVAC system to include all zone level and space level assumptions and parameters, and physical security requirements. Computerized analysis shall be prepared by using either a public domain program or the privately developed software programs. Provide lifecycle cost calculations. If not including CHP system in design, explain why not included. Submit the name and version of the program used for computerized analysis. (Prior approval by VA is required for the use of private programs, as opposed to public domain programs.) |  | F
M-2.2 | Calculations |  |  | Selected Concept Analysis |  |  | Provide 8,760-hour basis energy analyses together with the energy model to optimize the orientation and massing schemes being considered. Envelope and glazing are optimized; all other variables (occupancy, regulated and unregulated loads) in the energy model shall remain fixed for all schemes at this design phase submittal. For analysis, use ASHRAE latest climate data. |  | P | U | F
M-2.3 | Calculations |  |  | Life Cycle Cost Analysis |  |  | Conduct a complete life cycle cost analysis with heating and cooling requirements, include specific recommendations and full back‑up data. State the heating and cooling capacities of each departmental area used in the life cycle cost analysis. State the block cooling and heating loads for each new and/or existing building. |  | P | U | F
M-2.4 | Calculations |  |  | Load Calculations |  |  | Provide detailed zone heating and cooling load calculations, U-Factors, and psychometric analysis for each zone. Accompany these calculations with the architectural drawings 1/8"=1'-0" (1:100) scale and Model showing correlation between each zone boundary and the floor area and abbreviated/coded room numbers used with computer input data sheets. Also submit the input manuals for the computer programs with indications of the capabilities and limitations of the programs. Submit a level of detail of the calculations consistent with the development of the architectural drawings. |  |  | P | U | F
M-2.5 | Calculations |  |  |  | Air-Handlers |  | Estimate capacities in cubic feet per minute, static pressure, and required fan-motor horsepower for air-handling units, heating and ventilating units, and exhaust air systems. Use psychometric chart for each air-handling unit showing cooling and heating coil condition and computation of humidification loads. |  |  |  | F | R
M-2.6 | Calculations |  |  | Chilled Water Plant |  |  | For the proposed chilled water plant, submit:
M-2.7 | Calculations |  |  |  | Quantity |  | Quantity and type of chillers, capacity in tons of refrigeration, and the electrical requirements. |  |  |  | P | F
M-2.8 | Calculations |  |  |  | Pertinent Data |  | Pertinent data for the chilled water plant accessories, that is, chilled water and condenser water pumps, and cooling tower. |  |  |  | P | F
M-2.9 | Calculations |  |  |  | Coordination |  | Coordination of the cooling tower location with other disciplines for calculations on items related to cooling towers. |  |  |  | P | F
M-2.10 | Calculations |  |  |  | Acoustics/Dispersion |  | Updated sound/acoustic and dispersion analyses to ensure that the noise generated by the air-handling units and the fans comply with VA requirements and the design does not pose any potential for short-circuiting of air or health hazard due to emissions by cooling tower, emergency generator, or boilers. |  |  |  | P | F
M-2.11 | Calculations |  |  |  | Acoustics |  | Acoustic analysis of all systems and steps taken to ensure compliance with the specified noise levels in coordination with other disciplines. |  |  |  | P | F
M-2.12 | Calculations |  |  |  | Dispersion |  | Dispersion analysis for the cooling towers and hazardous exhausts as required by VA design manuals. |  |  |  | P | F
M-2.13 | Calculations |  |  |  | Recommendations |  | Make specific recommendations or efficiencies to improve the design, even if these recommendations exceed OSHA and ASHRAE requirements. Provide all calculations to support recommendations. |  |  |  | P | F
M-2.14 | Calculations |  |  |  | Backup |  | Provide back-up details and calculations of the chilled water optimization study and selected pumping arrangement. |  |  |  | P | F
M-2.15 | Calculations |  |  | Heating System |  |  | For the heating system, submit: |  |  |  | P | F
M-2.16 | Calculations |  |  |  | Heating Requirements |  | Total heating load based on the available information of the space heating requirements, domestic hot water load, humidification loads, and the equipment steam demand. |  |  |  | P | F
M-2.17 | Calculations |  |  |  | Zoning |  | Written description of the proposed zoning of the heating system indicating such features as distribution of ventilation load, perimeter heat load, and reheat load associated with air terminal units. |  |  |  | P | F
M-2.18 | Calculations |  |  | Energy Analysis |  |  | Energy analysis with optimized envelope and glazing properties, and all reductions necessary to achieve the federally mandated energy consumption target. State all occupancy, regulated and unregulated load assumptions, and schedule parameters used in the analysis. State all modeled system operational characteristics. Use actual equipment performance curves from the design selections (mechanical, plumbing, and lighting). |  |  | P | U | F
M-2.19 | Calculations |  |  | Preliminary Electrical Power |  |  | Electrical power requirements (normal and emergency). |  |  | P | U | F
M-2.20 | Calculations |  |  | Ventilation Rates |  |  | Ventilation rates in charts to show if all the spaces meet ASHRAE 62.1, ASHRAE 170 and VA Design Manual requirements. |  |  | P | F
M-2.21 | Calculations |  |  | Steam Consumption |  |  | Estimated steam consumption from all sources. |  |  | P | F
M-2.22 | Calculations |  |  | Room-by-room Calculations |  |  | Room‑by‑room heating and cooling load calculations. |  |  |  | P | F
M-2.23 | Calculations |  |  |  | Coil/Fan-Motor Gains |  | Coil entering and leaving conditions and fan-motor heat gains for supply and return air fans. |  |  |  | P | F
M-2.24 | Calculations |  |  |  | Balance Sheet |  | Room‑by‑room air balance sheet for each air-handling unit showing supply, return, exhaust, make‑up, and transfer air quantities with the required air balance, that is, positive, negative, or zero with respect to adjoining spaces. |  |  |  | P | F
M-2.25 | Calculations |  |  | Equipment Spreadsheet |  |  | Excel spreadsheet for each air-handling system. Provide the details of supply, return, exhaust, make-up, and relief air, for each room. In addition, for each room provide area, height, volume, value of one air change per hour, actual calculated air changes per hour, and required minimum air changes per hour. |  |  |  | P | F
M-2.26 | Calculations |  |  | HVAC Equipment |  |  | Complete engineering calculations and selection of major HVAC equipment, such as chillers, cooling tower, air-handling units, heating and ventilating units, return and exhaust fans, circulating pumps, and energy recovery equipment, heat exchangers, PRV stations, and humidification equipment. |  |  |  | P | F
M-2.27 | Calculations |  |  | Chiller Plant |  |  | Analysis for use of a chiller plant waterside-economizer cycle. |  |  |  | P | F
M-2.28 | Calculations |  |  | Flow & Head |  |  | Flow and head calculations for pumping systems for peak and minimum block loads. |  |  |  | P | F
M-2.29 | Calculations |  |  |  | Pumps |  | Final selection of all pumps with the pump head calculations based on the actual piping layout and takeoffs, and pressure drop through the equipment selected for the systems. |  |  |  | P | F
M-2.30 | Calculations |  |  |  | Fans |  | Final selection of all fans with the fan static pressure calculations based on the actual duct layouts and takeoffs, and static pressure drop through the equipment for the systems. (Detailed calculations are required even if variable speed drives are used.) |  |  |  | P | F
M-2.31 | Calculations |  |  |  | Expansion Tanks |  | Sizing and selection of all expansion tanks based on the actual piping layout and volume computation. |  |  |  | P | F
M-2.32 | Calculations |  |  |  | Convertors |  | Sizing and selection of all steam to hot water convertors and heat exchangers based on the flow requirement of each terminal unit, that is, duct-mounted reheat coil, box (air terminal unit). mounted reheat coil, unit heaters, convectors, finned tube radiators, and radiant ceiling panels. |  |  |  | P | F
M-3.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
M-3.1 | Drawings |  |  | Floor Plans |  |  | Submit Floor Plans depicting the following:
M-3.2 | Drawings |  |  |  | Distribution |  | 1/8"=1'-0" (1:100) scale HVAC floor plans for typical areas showing the proposed routing of the main air distribution and piping layouts. Ductwork and piping may be shown in single line. Provide other formats as per the VA BIM STANDARD. |  | P | U | U | F
M-3.3 | Drawings | [5 empty] | 1/8"=1'-0" (1:100) scale HVAC floor plans for all areas showing (at minimum) main supply, return, and exhaust air ductwork with sizes based on the updated calculations. Show single line ductwork floor plans for proposed main distribution ducts be provided starting at SD1. This helps to identify choke points and verify floor to floor heights. Finally, main ductwork should be shown in two line format starting at DD. |  | P | U | U | F
M-3.4 | Drawings |  |  |  | MERs |  | 1/4"=1'-0" (1:50)floor plans of the typical mechanical equipment rooms (MERs) with at least two cross-sections showing all floor and ceiling mounted equipment, major ductwork, and piping. Show all ductwork and piping. The floor plans should show clearance requirements. The footprints shown for AHUs and major equipment should be based on actual sizes of equipment from at least 3 manufacturers. |  |  | P | U | F
M-3.5 | Drawings |  |  |  | Mechanical Spaces BIM Walk-throughs |  | Live BIM walk-throughs of the mechanical spaces as defined in the VA BIM STANDARD. |  |  |  | P | F
M-3.6 | Drawings |  |  |  | Mechanical Rooms |  | Locations and sizes of all mechanical equipment rooms and principal vertical shafts. |  | P | U | F
M-3.7 | Drawings |  |  |  | Layout |  | Block layout of major pieces of equipment that coincide with one another in each mechanical equipment room. |  | P | U | F
M-3.8 | Drawings |  |  | Diagrams |  |  | Submit the following diagrams, as per the VA BIM STANDARD and below:
M-3.9 | Drawings |  |  |  | Single-Line |  | Single-line air and water flow diagrams of existing heating plants, cooling plants, air-handling processes, and zone level (not space level) air and water distribution for the proposed options. |  | P | U | F
M-3.10 | Drawings |  |  |  | Flow & Riser |  | Updated flow and riser diagrams for each type of the typical air handling systems, exhaust (general and special) systems, and all hydronic systems, such as: chilled water system, hot water system, steam system, and glycol heat recovery system. Submit existing capacities of these systems, where applicable, and new estimated loads with pumping arrangement, and control valves for complete understanding of existing systems to be used or interfaced with the new systems. |  |  |  | F
M-3.11 | Drawings | [5 empty] | Airflow relationship diagram indicating “clean” areas that are positively pressurized with respect to adjoining areas and the “dirty” areas that must be under negative pressure with respect to adjoining areas, limited to SPD, labs, ORs, vivarium, and isolation rooms. |  |  |  | F
M-3.12 | Drawings |  |  |  | Control Systems |  | Updated control diagrams for each type of typical air and hydronic system used for development in previous submission by providing written description of the sequence of operation on the floor plans. Explain the function and role of each control device and describe the safety/alarms and normal operating controls of each system. Submit a schedule showing electrical control interlock of each component. Submit a single-line diagram of the direct digital control architecture. |  |  |  | F
M-3.13 | Drawings |  |  |  | Outside/Exhaust/Relief Air |  | Note outside air, exhaust air, and relief air louvers. Resolve various items affecting louver location, considering other factors such as visibility, historical considerations, wind direction, noise, physical security requirements, hurricane and storms, and health hazard odors caused by short circuiting of air from exhaust from kitchen exhaust, fume hoods, isolation room exhaust, emergency generators, and truck waiting areas, to intake . |  |  | P | U
M-3.14 | Drawings |  |  |  | Temperature Control |  | Individual room air distribution and temperature control arrangement for a representative sample of typical spaces, such as patient bedrooms, operating suite, laboratory areas, and conference rooms, on duct and piping layouts. |  |  |  | U
M-3.15 | Drawings |  |  | Demolition Plans |  |  | Final demolition drawings indicating scope of work for demolition. |  |  |  | F
M-3.16 | Drawings |  |  | Phasing |  |  | HVAC work associated with phasing plan. (The phasing plan should be reviewed and approved by the VA Medical Center, in consultation with the VA PM, to address and resolve such issues as vacating occupied spaces and creating swing spaces, scheduling utility shutdowns, and addressing parking and traffic disruptions). |  |  | P | F
M-3.17 | Drawings |  |  | Design Coordination |  |  | Drawings and Models of the interstitial spaces reflecting layout and service access requirements of all utilities (HVAC, plumbing, electrical and others) and. Provide live BIM interactive reviews for all interstitial and mechanical areas per VA BIM STANDARD. |  |  | P | U | F
M-3.18 | Drawings |  |  |  | Clearances |  | Show duct and ceiling clearances, where ductwork crosses, with 1/4’ = 1’0” (1:50) scale for local sections. Show all ductwork, regardless of sizes and/or complexity of layout at true size. Refer to VA BIM STANDARD for modeling requirements. |  |  |  | P | F
M-3.19 | Drawings |  |  | Fire Protection |  |  | Provide and show necessary smoke and fire dampers and smoke detectors on floor plans, per applicable NFPA codes. |  |  |  | P | F
M-3.20 | Drawings |  |  | Ventilation Rates |  |  | Updated Ventilation rates in charts to show if all the spaces meet ASHRAE 62.1, and VA Design Manual requirements, dehumidification, and pressurization criteria for all spaces occupied, and unoccupied conditions. |  |  |  | P | F
M-3.21 | Drawings |  |  | Engineering Control Center |  |  | Planned capabilities, include the features of energy management and conservation. Submit a point schedule for analog/digital input/outputs to be included in Engineering Control Center (ECC). |  |  | P | U | F
M-3.22 | Drawings |  |  | Underground Piping |  |  | Extent of the outside chilled water and condenser water piping. Indicate how the piping shall be laid in tunnels, trenches, or by direct burial. For the direct burial layout, show a profile of the relative elevations of the new pipes with the existing utilities and define the scope of work where necessary for re-routing existing utilities. |  |  |  | P | F
M-3.23 | Drawings |  |  |  | Large Scale Floor Plans |  | HVAC floor plans for all mechanical equipment rooms, with at least two cross-sections taken at right angles to each other at 1/4” = 1’-0” (6.3500 mm) scale. Show all equipment located on roof and/or grade. Coordinate to show the walking pads in the Model and on the architectural drawings. |  |  | p | U | F
M-3.24 | Drawings |  |  |  | Small Scale Floor Plans |  | HVAC floor plans for all areas showing all ductwork and piping at 1/8"=1'-0" (1:100) scale. Include: |  |  |  | P | F
M-3.25 | Drawings |  |  |  |  | Duct Pressure | Duct pressure classification on the floor plans for all air distribution systems. Identify the duct sections with demarcation symbols where the change in pressure rating takes place. |  |  |  | P | F
M-3.26 | Drawings |  |  |  |  | Duct and Pipe Sizes | All duct/pipe sizes and air/fluid quantities. Ductwork and piping on separate drawings. |  |  |  | P | F
M-3.27 | Drawings |  |  |  |  | Layouts | Utilities layout and accessibility of equipment for servicing and maintenance in the interstitial spaces. |  |  |  | P | F
M-3.28 | Drawings |  |  |  |  | Quantities | Air quantities for each room and each air inlet/outlet, expressed in cubic feet per minute, and fluid quantity (where required) in gallons per minute (liters per second). |  |  |  | P | F
M-3.29 | Drawings |  |  |  |  | Accessories | All volume dampers, fire dampers, smoke dampers, automatic control dampers, rises and drops in ductwork, and air inlets/outlets, on the air distribution floor plans. |  |  |  | P | F
M-3.30 | Drawings |  |  |  |  | Specialties | All piping specialties, such as expansion loops, anchors, valves, drip assemblies, and balancing fittings, on the piping floor plans and drain valves at low-points. |  |  |  | P | F
M-3.31 | Drawings |  |  |  |  | Room Name/Numbers | Indicate architectural room names and numbers. |  |  | P |  | F
M-3.32 | Drawings |  |  |  |  | Smoke/Fire Barriers | Identify all smoke and smoke/fire barriers. |  |  | P | U | F
M-3.33 | Drawings |  |  |  |  | Smoke/Fire Partitions | Identify smoke and fire partitions in HVAC floor plans.. |  |  | P | U | F
M-3.34 | Drawings |  |  |  | Water Distribution |  | Outside chilled water and condenser water distribution showing pipe sizes and insulation with plans, profile, sections, details, and all accessories, such as, anchors, expansion loops/joints, valves, manholes, capped and flanged connections, and the interface between the new and existing work. Show rerouting any utilities, cuttings of roads, pavements, and trees, as well as the extent of new and demolition work. |  |  | P | U | F
M-3.35 | Drawings |  |  |  | Temperature Control |  | Automatic temperature control drawings. Show all duct detectors, control valves/dampers static pressure sensors, and differential pressure control assemblies, whose actual physical location is critical for the intended sequence of operation on floor plans. For projects involving a central Engineering Control Center (ECC), provide a point schedule with intended analog/digital input/outputs, graphics capabilities, and requirements of the other trades to be included in the ECC. Provide a riser diagram showing locations of all field data-gathering panels and their interface with the ECC. Show the actual location of the ECC and peripherals on floor plans. The written sequence of operation describing the role of each individually numbered device should be shown on the floor plans on the same drawing on which the control schematic diagram is shown. Do not write the sequence in the specifications. Each sequence should describe the start-up, capacity control, safeties, morning warm-up cycle where applicable, and night setback cycle where applicable. |  |  |  | P | F
M-3.36 | Drawings |  |  |  | Details |  | Edit VA details to suit the project. Include any special details deemed useful and necessary for the project. |  |  |  | P | F
M-3.37 | Drawings |  |  |  | Demo |  | HVAC demolition drawings showing the extent of demolition work. Indicate sizes of ductwork and piping to be dismantled. Show capacities and sizes of the existing equipment to be removed. Show points of connection, disconnection, blank-offs, and dead-end flanges with isolating valves. Coordinate demolition and restoration work with other disciplines. State the revised capacities of the existing systems affected by the demolition work together with additional efforts involved in testing, balancing, and adjusting them. |  |  | P | U | F
M-3.38 | Drawings |  |  |  | Architecturally Significant Equipment (ASE) |  | Provide plans at 1/4” = 1’0” (1:50) scale showing location and sizing of utility connections to ASE identified equipment. |  |  | P | F | R
M-3.39 | Drawings |  |  |  | Schedules |  | Updated schedules of equipment that includes chillers, boilers, pumps, air handling units, terminal units, cooling towers, and all equipment required for operations. |  |  | P | U | F
M-3.40 | Drawings |  |  | Steam and Condensate Piping |  |  | Drawings should include aspects of condensate control (piping slope, locations of traps, flash tanks), and flexibility/expansion features (anchors, expansion compensation, flexible connectors). |  |  | P | U | F
|  | STEAM DISTRIBUTION (OUTSIDE) |  |  |  |  | VA submission requirements for Outside Steam Distribution
SD-1.0 | Report |  | BASIS OF DESIGN
SD-1.1 | Report |  |  | Narrative |  |  | Provide a Narrative describing the following:
SD-1.2 | Report |  |  |  | Life Cycle Cost Analysis |  | Life cycle cost analysis for alternative types of steam distribution systems and alternative routings of the systems. Analyze the test results on existing systems (where applicable). Evaluate the alternatives, consider all other relevant issues, and make recommendations. |  |  | P | F
SD-1.3 | Report |  |  |  | Geotechnical |  | Confirmation of acceptable soil conditions related to classification of underground factory-fabricated pre-engineered systems, if used. |  |  | P | F
SD-2.0 |  |  | CALCULATIONS
SD-2.1 | Calculations | [5 empty] | Provide steam and condensate loads that shall be imposed on new or existing distribution facilities. |  |  | P | F
SD-2.2 | Calculations | [5 empty] | Provide calculations of pipe sizing. |  |  | P | F
SD-2.3 | Calculations | [5 empty] | Provide dispersion analysis for boilers. |  |  | P | F
SD-2.4 | Calculations | [5 empty] | Provide performance requirements for all steam traps. |  |  | P | F
SD-2.5 | Calculations | [5 empty] | Provide pipe stress calculations. Select the proper expansion facilities for piping in manholes, tunnels and trenches. |  |  | P | F
SD-3.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
SD-3.1 | Drawings |  |  | Site Plan |  |  | Submit a site plan indicating:
SD-3.2 | Drawings | [5 empty] | Description of distribution systems including locations of all manholes and pipe expansion devices. |  |  | P | U | F
SD-3.3 | Drawings | [5 empty] | Overall dimensions and arrangement of major piping in trenches and tunnels and other underground utilities. |  |  |  | P | F
SD-3.4 | Drawings | [5 empty] | Scaled drawings at 1/4” =1’0” (1:50) of plan views and sections of manholes. |  |  |  | P | F
SD-3.5 | Drawings | [5 empty] | Concrete trench, access, and tunnel drawings, indicating the basic piping layout and pipe supports in plans and sections. List all safety devices required. Show standard details for safety device testing requirements for each device. |  |  |  | P | F
|  | STEAM GENERATION |  |  |  |  | VA submission requirements for Steam Generation
SG-1.0 | Report |  |  | Assessment |  |  | Submit an initial assessment including the following:
SG-1.1 | Report | [5 empty] | Information on proposed system steam pressures, types of condensate return systems (pumped, gravity, vacuum), and line sizes. |  | P | U | F
SG-1.2 | Report |  |  |  | Alternatives |  | Description of viable alternatives for generating steam. Alternatives normally include: new steam plant, use of existing steam generation facilities if there is sufficient additional capacity, modification of existing steam generating facilities, or purchase of steam. Consider hot water generation. Submit rationale for the selection or rejection of the alternatives. |  | P | U | F
SG-1.3 | Report |  |  |  | Equipment |  | List of the steam plant equipment alternatives that shall be evaluated. Typical alternatives include fire tube and water tube boilers, types of heat recovery equipment, and types of pumps. |  | P | U | F
SG-2.0 |  |  | BASIS OF DESIGN
SG-2.1 | Report |  |  | Narrative |  |  | Submit a narrative describing the following:
SG-2.2 | Report | [5 empty] | When a new steam generating facility is an alternative, identification of the types of fuels that are to be evaluated. Submit rationale for selection or rejection of any of the listed fuels. |  | P | U | F
SG-2.3 | Report | [5 empty] | Metering requirements coordinated with the ongoing activities at the existing facilities, and provide a brief description of the scope of work and extent of coordination involved. |  | P | U | F
SG-2.4 | Report | [5 empty] | Combined new (estimated) and existing steam loads, including maximum and minimum summer and winter demands and total annual production. Provide breakdown of new steam loads into categories of end use, such as building heating, humidification, reheat, domestic hot water, sterilization, line losses, kitchen, and laundry. |  | P | U | F
SG-2.5 | Report | [5 empty] | Initial selection of major equipment and preliminary calculations of equipment sizing. |  |  | P | F
SG-3.0 |  |  | CALCULATIONS
SG-3.1 | Calculations |  |  | Initial Calculations |  |  | Submit estimated steam and condensate loads to be carried by the systems. |  | P | U | F
SG-3.2 | Calculations | [5 empty] | Estimate peak steam demands for the new facilities and any change in existing steam demands. |  | P | U | F
SG-3.3 | Calculations | [5 empty] | Determine existing maximum and minimum summer and winter steam demands and total annual production, if a steam plant exists. Submit a verification of the accuracy. Include a graph showing the relationship between outside temperature and winter steam demands. |  | P | U | F
SG-3.4 | Calculations |  |  | Life Cycle Cost Analysis |  |  | Provide life cycle cost analysis of the steam supply alternatives, including fuel selection. Include analysis of alternative plant locations. Compare the alternatives, present test results on existing equipment and systems, evaluate all other relevant issues, and make recommendations. |  |  | P | F
SG-3.5 | Calculations | [5 empty] | Provide life cycle cost analysis for alternatives types of equipment to be applied and for heat-recovery alternatives. |  |  | P | F
SG-3.6 | Calculations | [5 empty] | Provide data on emissions regulations and the methods for compliance. |  |  | P | F
SG-3.7 | Calculations | [5 empty] | Provide pipe hanger load calculations and locations. |  |  |  | P | F
SG-3.8 | Calculations | [5 empty] | Provide performance requirements for all control and regulating valves, flow meter systems, steam traps, and heating and ventilating systems. |  |  |  | F
SG-3.9 | Calculations |  |  | Submissions |  |  | Determine sizing of all major piping systems based on pipe and pump selections for actual arrangement of the piping systems. Refine calculations. Submit catalog cuts of two manufacturers on all equipment selections. |  |  |  | P | F
SG-3.10 | Calculations | [5 empty] | Provide refined steam load and equipment sizing for all major equipment, including boilers, pumps, heat recovery devices, tanks, and emissions control devices. |  |  |  | P | F
SG-3.11 | Calculations | [5 empty] | Conduct a stress analysis under all heating loads on piping systems to include each possible valve configuration. |  |  |  | P | F
SG-4.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
SG-4.1 | Drawings |  |  | Preliminary Drawings |  |  | Indicate location of the existing steam plant and alternative locations of new or expanded steam generating facilities, as applicable. Show outside fuel related storage and handling facilities. |  | P | F
SG-4.2 | Drawings | [5 empty] | Provide plan layouts of alternatives for new plant or modification to existing plant, showing location of equipment and personnel facilities. |  |  | P
SG-4.3 | Drawings | [5 empty] | Indicate final location of new steam generating facilities on a site plan. |  |  |  | F
SG-4.4 | Drawings | [5 empty] | Provide single-line flow diagrams of all systems, feed water, steam, and condensate. (existing and proposed options). |  |  | P | F
SG-4.5 | Drawings | [5 empty] | Indicate sections of the steam plant showing major equipment, major piping systems, and personnel facilities. |  |  |  | P | F
SG-4.6 | Drawings | [5 empty] | Indicate locations of all equipment, major piping, and pipe supports in plans and sections. Show demolition work. Draw plans and sections at 1/4” = 1’0” (1:50) scale. |  |  |  | P | F
SG-4.7 | Drawings | [5 empty] | Provide schedules, equipment lists, and site plans. |  |  |  | P | F
SG-4.8 | Drawings | [5 empty] | Show access to all equipment and valves that require normal maintenance, testing, or operation to include by-pass valves. DA Tank access to manways, sight glasses, relieve valve. Boiler and economizer access to all valves. Header Valve access, flow meters, make up valves and by-passes, etc. |  |  |  | P | F
SG-4.9 | Drawings | [5 empty] | Provide schematic control diagrams for the burner management system and flame safeguard systems. |  |  |  | P | F
SG-4.10 | Drawings |  |  |  | Emissions |  | Verify that a check for changes in applicable emissions regulations that may affect the design or operation of the steam plant has been performed and any necessary changes have been made to the final design. |  |  |  | P | F
|  | WASTE DISPOSAL SYSTEMS |  |  |  |  | VA submission requirements for Incineration/Waste Disposal
WD-1.0 |  |  | BASIS OF DESIGN
WD-1.1 |  |  |  | Alternatives for Waste Disposal |  |  | Submit an Basis of Design (BOD) report including:
WD-1.2 | Report | [5 empty] | Analysis of viable alternatives for waste disposal and recommended solution. Give rationale for the selection or rejection of alternatives. |  | P | U | F
WD-1.3 | Report | [5 empty] | Description of the proposed systems and equipment. Include quantities and function. Identify and address any related physical security needs. |  |  | P | F
WD-1.4 | Report | [5 empty] | Provide equipment selections. |  |  |  | P | F
WD-1.5 | Report | [5 empty] | Discussion of the existing systems and proposed options including:
WD-1.6 | Report | [5 empty] | Verification of changes in applicable emissions regulations that may affect the design or operation of the incineration system has been performed. |  |  | P | U | F
WD-1.7 | Report | [5 empty] | Verification that any design changes due to applicable emissions regulations changes has been used in the final design. |  |  |  | P | F
WD-1.8 | Report |  |  | Site Assessment |  |  | Site considerations such as clean/dirty side - dumpster/dock requirements. | P | U | F
WD-2.0 |  |  | CALCULATIONS
WD-2.1 | Calculations |  |  | Calculations |  |  | Estimate the types and quantities of waste that shall be generated by the new facility. Provide life cycle cost analysis on the alternatives for waste disposal. Compare the alternatives, present test results on existing systems (if applicable), evaluate all other relevant issues, and make recommendations. Provide load calculations on the amount and types of waste and equipment sizing calculations. |  | P | U | F
WD-2.2 | Calculations | [5 empty] | Identify emissions control devices. |  |  | P | F
WD-3.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
WD-3.1 | Drawings |  |  | Plans |  |  | Submit site plan indicating alternatives for locating an incinerator system. Indicate the location of the existing incinerator, if applicable. |  | P | U | U
WD3.2 | Drawings | [5 empty] | Submit plan view layout of new system or modification to existing system showing locations of major equipment. |  |  |  | P | F
WD-3.3 | Drawings | [5 empty] | Provide 1/4” = 1’0” (1:50) scale plans and sections indicating major equipment. |  |  |  | P | F
WD-3.4 | Drawings | [5 empty] | Submit locations of all equipment and major piping on 1/4” = 1’0” (6.3500 mm) scale plans and section. Identify and locate HVAC controls, air filtration and circulation. |  |  |  | P | F
WD-3.5 | Drawings | [5 empty] | Indicate demolition work on 1"= 50.0' (site plans) and 1/4” = 1”0” (1:50) for interior scale plans and sections. |  |  |  | P | F
WD-3.6 | Drawings |  |  | Schedules |  |  | Submit completed schedules and equipment lists. |  |  |  | P | F
VA SME
| Asesh Raychaudhuri |  |  |  |  | Asesh.Raychaudhuri@va.gov
| Don Walden |  |  |  |  | Don.Walden@va.gov
| Doug Ryan |  |  |  |  | Douglas.Ryan@va.gov

## Electrical
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 | [5 empty] | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | ELECTRICAL |  |  |  |  | VA submission requirements for Electrical
E-1.0 |  |  | BASIS OF DESIGN |  |  |  | Submit the Basis of Design (BOD) at each phase with updated information. Report to include:
E-1.1 | Report |  |  | Narrative |  |  | Indicate electrical design approach proposed in narrative form. Determine whether the existing site utility service and distribution, switchgear, primary feeders, power transformers, and distribution equipment are adequate for the new loads for normal, stand-by, and essential electrical systems. |  | P | U | U | F
E-1.2 | Report |  |  | Utility Company |  |  | Provide detailed description of the extent of new utility work (if required). |  | P | F
E-1.3 | Report |  |  | Physical Security |  |  | Provide description of physical security requirements and implementation into electrical design. |  | P | U | F
E-1.4 | Report |  |  | Uninterruptible Power System (UPS) |  |  | Determine requirements for uninterruptible power system (UPS) and description of loads to be served. (Comply with PSDM for telecommunications areas). |  | P | U | F
E-1.5 | Report |  |  | Building Electrical Power Requirements |  |  | Provide description of loads associated with essential electrical system and/or stand-by electrical power system to determine preliminary emergency and/or stand-by electrical power generation capacity required to support the building electrical power requirements. |  | P | U | F
E-1.6 | Report |  |  | Existing Electrical Systems |  |  | Provide a plan describing the impact of the new construction work to the existing electrical power distribution systems. Describe how connection to existing electrical distribution system will occur. |  | P | U | F
E-1.7 | Report |  |  | Present Demand Load |  |  | Present demand load (medium voltage switchgear and primary feeder) and projected additional load of new construction. |  | P | U | U | F
E-1.8 | Report |  |  | Electrical Design Alternatives |  |  | Two design options (campus and building level) for the electrical power distribution systems and a list of advantages and disadvantages for each. Include description of physical security requirements and implementation into electrical design alternatives. |  | P | F
E-1.9 | Report |  |  | Electrical Design Approaches |  |  | Descriptions of the electrical design approaches for the specialty areas (including but not limited to X-rays Rooms, Intensive Care Units and Operating Room Suites) that shall be submitted for DD1. |  | P | U | U | F
E-1.10 | Report |  |  | Determination Method |  |  | Provide methodology by which fault current, protective device coordination, arc flash, generator sizing, load, feeder and equipment sizing, voltage drop, harmonic distortion, lightning protection risk analysis, and lighting calculations, grounding system design and initial testing requirements were made. |  | P | U | F
E-1.11 | Report |  |  |  | Emergency Power |  | Identify the type of emergency power needed; address and classify per NFPA 110/111. |  | P | U | U | F
E-1.12 | Report | [5 empty] | Evaluate use of battery back-up vs. generator power for life safety equipment. |  | P | U | U | F
E-1.13 | Report | [5 empty] | Identify largest load of mechanical systems. |  | P | U | F
E-1.14 | Report | [5 empty] | Largest changes or changes to mechanical systems. |  | P | U | F
E-1.15 | Report | [5 empty] | Evaluate using BMS systems for managing loads on generator power. |  | P | U | U | F
E-1.16 | Report |  |  |  | Distribution Panel |  | For shelled rooms to be built-out later provide distribution panels of appropriate size to similar equipment. |  | P | F
E-1.17 | Report |  |  | Life Cycle Cost |  |  | Report of the life cycle cost analyses for major electrical distribution system equipment options. Indicate the recommended design and equipment. |  | P | F
E-1.18 | Report |  |  | Existing Facility Demand Load |  |  | Existing facility demand load (medium voltage switchgear and primary feeder) and projected additional load of new construction based on square footage. |  | P | F
E-1.19 | Report |  |  | Description of Methods |  |  | Description of methods to determine fault current, protective device coordination, arc flash, generator sizing, load, feeder and equipment sizing, voltage drop, harmonic distortion, lightning protection risk analysis, and lighting calculations. |  | P | F
E-1.20 | Report |  |  | Lighting Control Systems |  |  | Description of Lighting Control Systems. |  | P | F
E-1.21 | Report |  |  | Electrical Site Design |  |  | Description the following Electrical Site design requirements:
E-1.22 | Report |  |  |  | Redundant Power Requirements |  | Redundant power requirements and strategy (i.e. primary selective or radial). |  | P | F
E-1.23 | Report |  |  |  | Back-Up Generator Type |  | Describe implementation of back-up generator type as identified by the VA during the requirements definition. (i.e. Central Plant generators or on-site generators). |  | P | F
E-1.24 | Report |  |  |  | Utility Company Requirement |  | Provide previous submission documents modified to meet the utility company's requirements. Update the written summary of proposed electrical service/methods/equipment based on discussions and agreements with the electrical utility. |  | P | F
E-1.25 | Report |  |  | Room Data Sheet |  |  | Coordinate electrical requirements on room data sheets. (See Architectural requirements.) |  |  | P | F
E-1.26 | Report |  |  | Life Cycle Cost |  |  | Report of the life cycle cost analyses for two lighting systems options. Indicate the recommended design and equipment (i.e. LED or fluorescent). |  |  | P | F
E-1.27 | Report |  |  | Cut Sheets |  |  | Provide major equipment cut sheets for primary and secondary electrical distribution systems. |  |  | P | F
E-1.28 | Report |  |  | Utility Company Correspondence |  |  | Provide copies of all correspondence and minutes of meetings with all utility company representatives. | P | U | U | U | F
E-1.29 | Report |  |  | Utility Company Incoming Service |  |  | Provide written approval by the utility company of the design of the electrical incoming service. | P | U | U | U | F
E-1.30 | Report |  |  | Utility Company Incoming Service |  |  | NFPA 99 risk analysis for wet procedure locations to determine which operating, surgical delivery, or other patient care areas shall be designated as wed procedure locations. |  |  | P | F
E-1.31 | Report |  |  | Code and Criteria |  |  | Identify design references, (VA design guides, NEC, IEE, NFPA, etc.) |  |  | P | F
E-1.32 | Report |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  |  | Analyze impact of seismic correction plan on all electrical systems. Determine minimal acceptable changes necessary to implement seismic corrections. | P | U | U | F
E-2.0 |  |  | CALCULATIONS
E-2.1 | Calculations |  |  | Existing Peak Demand |  |  | Existing peak demand readings at point of connection to serve new equipment/building. |  | P | F
E-2.2 | Calculations |  |  | Normal Power System |  |  | Normal power system load calculations to support electrical equipment sizing and ratings. 'Demand factors' based on the type of load, needs to be applied. |  | P | U | U | F
E-2.3 | Calculations |  |  | Stand-By Power System |  |  | Stand-by power system load calculations associated with essential electrical system and/or stand-by electrical power system to determine emergency and/or stand-by electrical power generation capacity required to support the building electrical power requirements. 'Demand factors' based on the type of load, needs to be applied. |  | P | U | U | F
E-2.4 | Calculations |  |  | Electrical Systems |  |  | Estimated connected loads based on panel schedules for each area function’s lighting and power, normal and essential electrical systems. 'Demand factors' based on the type of load, needs to be applied. |  |  |  | P | F
E-2.5 | Calculations |  |  | Panel and Switchboard |  |  | Panel and switchboard schedules for load analysis. 'Demand factors' based on the type of load, needs to be applied. |  |  |  | P | F
E-2.6 | Calculations |  |  | Generator Sizing |  |  | Generator sizing calculation based upon input loads by Automatic Transfer Switch (ATS) system, load steps. Apply seasonal demands to narrow down the generation capacity of the essential power system. 'Demand factors' based on the type of load, needs to be applied. |  |  | P | U | F
E-2.7 | Calculations |  |  | Lightning Protection |  |  | Lightning protection risk analysis. |  | P | F
E-2.8 | Calculations |  |  | Generator Fuel Storage |  |  | Generator fuel storage requirements. |  |  | P | F
E-2.9 | Calculations |  |  | Faults and lighting |  |  | Fault current, protective device coordination and lighting calculations. |  |  |  | P | F
E-2.10 | Calculations |  |  | Faults |  |  | Provide calculations for arc flash, voltage drop, harmonic distortion. |  |  |  | P | F
E-3.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
E-3.1 | Drawings |  |  | Utilities |  |  | Identify, locate, and determine capacity (if applicable) of normal power, emergency power, and pathways for low voltage systems. |  |  | P | U | F
E-3.2 | Drawings |  |  |  | Site Plan |  | Provide site plan showing impact of proposed new work on the existing site and distribution, indicating new and existing locations of incoming utility electrical power service, underground electrical vaults, manholes, duct banks, and utility tunnels. Show major electrical work with respect to locations of substations and transformers. | F
E-3.3 | Drawings |  |  |  | One-Line Diagram |  | Provide proposed, conceptual one-line diagram for medium voltage (below 69kV) and low voltage (below 600V) electrical power distribution system. One-line diagram shall show major normal, essential electrical, and standby electrical system, main electrical components, and the correlation between the systems. |  | P | U | U | F
E-3.4 | Drawings |  |  |  | Main Electrical Areas |  | Plans showing locations of main electrical areas, such as main electrical switchgear, main electrical vaults, generator rooms, and/or energy center and indicating their approximate dimensions. On the plans, show outlines of major electrical equipment items in these rooms, nurse call, PA, intercom and outlines of minimum working clearance as required by the applicable National Electrical Code. | P | U | U | F
E-3.5 | Drawings |  |  |  | Lighting Plan(s) |  | Plans showing proposed lighting for key rooms/areas (i.e. public lobbies, conference rooms, patient rooms). |  |  | P | U | F
E-3.6 | Drawings |  |  | CONSTRUCTION DRAWINGS and MODELS |  |  | As per the VA BIM STANDARD and below
E-3.7 | Drawings |  |  |  | Main Electrical Areas |  | Provide plans (main electrical room layouts) at 1/4” = 1’0” (1:50) minimum scale. Electrical equipment rooms and electrical closets shown stacked vertically. Show all electrical power distribution equipment to scale. Include clearances for installation in front, side and top as per NEC' required clearances for safety, maintenance, and operation of equipment. Mechanical ductwork, water pipes, etc. do not run over panels. |  |  | P | U | F
E-3.8 | Drawings |  |  |  | Site Plan |  | Site plan(s) showing existing and proposed new underground work for electrical power distribution system. Coordinated drawings shall show all new services to site and buildings; all new medium voltage cable installations; all manholes, duct banks, transformers, roadway, parking, and grounds lighting; and the medium voltage service point. |  | P | U | U | F
E-3.9 | Drawings |  |  |  | Demolition Plan |  | Demolition drawings, indicating scope of work for demolition, spaces to be made available from demolition, and construction phasing impacts of demolition. |  |  | P | U | F
E-3.10 | Drawings |  |  |  | One-Line Diagram |  | System furniture wiring requirements (If applicable) |  |  | P | F
E-3.11 | Drawings |  |  |  | Lighting Plan |  | Provide 1/8” = 1’-0” (1:100) scale floor plans that show all power, signal, and lighting layouts. Lighting for key rooms/areas. Show room titles on floor plans. Show location of all equipment, lighting fixtures, outlets, and devices. Provide complete wiring/circuiting of devices and equipment. Show motor protective devices, and controller and feeder sizes. Show proposed phasing scheme of electrical work if applicable. |  |  | P | U | F
E-3.12 | Drawings |  |  |  | Architecturally Significant Equipment (ASE) |  | Provide 1/4” = 1’0” (1:50) scale plans showing location and sizing of utility connections to ASE identified equipment. |  |  | P | F | R
E-3.13 | Drawings |  |  |  | Legend |  | Provide legend symbol list, abbreviations, details and schedules. Schedules shall include transformer, distribution switchboard, distribution panelboards, and branch-circuit panel board load schedules. |  |  | P | U | F
E-3.14A63:Q71F67AA66:Q71 | Drawings |  |  | Final Drawings |  |  | Final drawings signed and sealed by Engineer of Record registered in the jurisdiction where the project is to be built. |  |  |  |  | F
VA SME
| Dat Tran |  |  |  |  | Dat.Tran2@va.gov
| Larry Lau |  |  |  |  | Larry.Lau@va.gov

## Telecommunications
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAMEAA8:Q30 | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 | [5 empty] | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | TELECOMMUNICATIONS |  |  |  |  | VA submission requirements for Telecommunications
T-1.0 |  |  | BASIS OF DESIGN |  |  |  | Submit the Basis of Design (BOD) report updated at each submittal with the following information:
T-1.1 | Report |  |  | Narrative |  |  | Narrative descriptions must include design, basic assumptions, compatibility with existing FMS & OIT Communications equipment, systems, TIP, Circulating Communications Grounding System (CCGS), Communications lightning Protection Systems (CLPS) and points of interconnection with existing communications systems; especially, if in an Historic Designated Facility. |  | P | U | U | F
T-1.2 | Report |  |  |  | Major Systems |  | Identification of major telecommunication systems for project. |  | P | U | F
T-1.3 | Report |  |  |  | Subsystems |  | Identification of FMS, OIT, Emergency and Safety Communications equipment use location of TIP, including conduit, race ways, cable trays and cable management for project. |  |  | P | U | F
T-1.4 | Report |  |  |  | System Compliance |  | Confirmation FMS, Emergency, Safety, and OIT Communication Equipment and Systems are compliant with most current applicable Federal Codes, Standards (including local) VA design manuals and guides. |  |  | P | U | F
T-1.5 | Report | [5 empty] | Confirm FMS, Emergency, Safety and OI&T Communications Equipment and Systems design is compliant with Division 26, 27 & 28 Master Specifications. |  |  | P | U | F
T-1.6 | Report |  |  |  | Programming Differences |  | Reconcile differences between programming and interface(s) required in FMS, Emergency, Safety and OI&T Equipment and Systems in all Communications Areas, Spaces and Locations.” |  |  | P | F
T-1.7 | Report |  |  |  | Interdisciplinary Coordination |  | Determine the cooling needs for communication equipment. |  |  | P | F
T-1.8 | Report | [5 empty] | Confirm coordination with installation of other equipment. |  |  | P | U | F
T-1.9 | Report | [5 empty] | Identify and define any proprietary systems to be used. |  |  | P | F
T-1.10 | Report | [5 empty] | Identify power requirements for telecom needs. Detail the planned power density of equipment at the IT equipment enclosure level at ultimate design loading conditions. Describe how power capabilities will increase to achieve ultimate design loads in the design. |  |  | P | F
T-1.11 | Report | [5 empty] | Identify HVAC requirements for telecom needs. Detail the HVAC systems and operating parameters planned for entrance rooms, MCR, and TRs. Describe how HVAC capabilities will increase to achieve ultimate design loads in the design. |  |  | P | F
T-1.12 | Report | [5 empty] | Describe how the Computational Fluid Dynamics (CFD) assessment of the design of the MCR at commissioning load, ultimate design load, and in all contingency conditions satisfies the environmental parameters of published standards. Describe the process, setpoints, and outcomes of the CFD analysis. |  |  | P | F
T-1.13 | Report |  |  |  | Expandable Design |  | Ensure design of FMS & OIT Communications Systems pathways and Telecommunications Rooms accommodates an increase of 40% for future expansion. |  | P | U | F
T-1.14 | Report |  |  |  |  | LED Lighting | Assess additional requirements on Telecommunications for new technologies such as advancements in LED lighting. |  |  | P | F
T-1.15 | Report |  |  |  |  | Power over Ethernet (PoE) requirements | Perform Risk Assessment AND Cost Benefit Analysis (CBA) FOR EACH (Unless OEM incorporates PoE as a part of their equipment and system), FMS, Critical, Emergency, Life & Public Safety, Medical and OIT Communications Equipment and Systems THAT MAY REQUIRE BICSI CAT 6A cable, and incorporate estimated PoE requirements for other systems (etc. lighting, electrical, etc.) to determine TOTAL COST AND SITE PREP IMPACT FOR PROJECT. Each equipment AND system require this study on a case-by-case bases. |  |  | P | F
T-1.16 | Report |  |  |  | Location of Telecommunications Spaces |  | Confirmation that telecommunications spaces are not located next to elevator machine room, electrical room, surgical room and associate areas, radiology, MRI et cetera. |  | P | F
T-1.17 | Report |  |  |  |  | FMS | Provide specific description of the required FMS Emergency Voice System (not VoIP or call manager) function and operation ensuring it replaces the PBX that normally handles them. Ensure location, type, and quantity for required FMS emergency voice (not VoIP or call manager) interfaces and operates with like communications systems. Use CFM approved TIL Master Specification 27 31 00-Emeergency Voice Switching Equipment and System; or, 27 31-31 Emergency Voice Switching Equipment and System Extension for this purpose. |  | P | F
T-1.17.1 | Report |  |  |  |  | DAS | Distributed Radio Antenna (Within Building) Equipment and System (DAS), ensure the DAS is provided in each VA Medical and Administrative Facility, per Homeland Security (HLS) direction after 9-11. Use CFM Approved TIL Specification 27 53-19 – DISTRIBUTED RADIO ANTENNA (WITHIN BUILDING) EQUIPMENT AND SYSTEM. Ensure the edited specification specifically describes and requires the DAS is used FOR ONLY EMERGENCY RESPONDER USE WITH NO ADD ONs. |  | P | U | U | F
T-1.18 | Report |  |  |  |  | TIP | Description of location, type, and quantity for required patient phone equipment type and numbers and TIP support. |  | P | F
T-1.19 | Report |  |  |  |  | Cabling | Determination of TIP FMS & OIT cabling requirements, types, counts and accessories. Insure all national code analog equipment and cables types and counts are addressed. |  | P | U | F
T-1.20 | Report |  |  |  |  | Sizing | Confirmation that telecommunications space physical sizing, interconnection and locations are addressed. |  | P | U | F
T-1.21 | Report |  |  |  |  | Calculations | Show calculations for the following systems. a. Television loss calculations for coax based systems b. Antennae systems calculations for signal level and loss. c. Public Address Amplifiers Power calculations. d. Outside plant copper pair count calculation e. Copper pair riser cable calculations |  |  | P | U | F
T-1.22 | Report |  |  |  |  | MCR | If new MCR is being constructed, description of structured cabling backbone between new MCR and campus TRs. Describe how existing MCR-TR fiber backbone will be switched over to new diverse path MCR-TR fiber backbone runs terminating in the new MCR. |  | P | U | F
T-1.23 | Report |  |  |  |  | MCR | If new MCR is being constructed, description of structured cabling elements within the MCR (between MDAs and HDAs and between HDAs and server cabinets). |  | P | U | F
T-2.0 |  |  | VA ACQUISITION CODES
T-2.1 | Aggregate |  |  | Supplier/Installer |  |  | Provide VA Acquisition Codes for all telecommunications cabling and equipment to identify who is responsible for supplying/installing - Provide Responsibility Matrix. |  |  | P | U | F
T-3.0 |  |  | APPROVALS
T-3.1 | Report |  |  | AHJ Approval |  |  | TIP, FMS, and Spectrum Management verified by AHJ SMCS (see TDM). Contact AHJ SMCS for technical assistance if required at any point throughout the design. Telecommunications space (entrance rooms, MCR, TRs) verified by OIT Data Center & Infrastructure Engineering project. |  | P | U | F
T-3.2 | Report |  |  | Utility Company Approval |  |  | Describe the extent of utility company work required. Include copies of all correspondence and minutes of meetings with all utility company's representatives. |  | P | U | F
T-3.3 | Report | [5 empty] | Provide copies of all correspondence and minutes of meetings with utility company representatives. Include a written summary of any conversations with the telecommunications utilities. |  | P | U | U | F
T-3.4 | Report | [5 empty] | Provide written approval by the telecommunications utility companies of the design for incoming services. |  |  | F
T-4.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
T-4.1 | Drawings |  |  | Symbols, Notes, & Abbreviations |  |  | Include a drawing identifying telecommunications symbols, notes and abbreviations for the 2D documentation. |  | P | U | U | F
T-5.0 |  |  |  | Diagrams |  |  | Submit the following diagrams:
T-5.1 | Drawings |  |  |  | Phasing |  | Proposed Phasing for FMS Special and OIT Communications work. |  |  | P | U | F
T-5.2 | Drawings |  |  |  | Conceptual |  | Updated conceptual diagrams for proposed FMS Special Communications and OI&T Communication Infrastructure System Plant (TIP). |  | P | U | F
T-5.3 | Drawings |  |  |  | Zoning |  | Zoning diagram for above ceiling utilities. Show the areas served by each FMS Special Communications and OIT telecommunications room and for the zones for the Public Address system. Zoning diagram should detail the floor area served by each Telecommunications Room to ensure that maximum cable distances between the TR and the work area outlets is within specification. Zoning diagram should also include all telecommunications services supported by each TR, including video distribution, nurse call, et cetera. Show pathways and conveyance equipment, identifying capacities and proposed cable loads. |  |  | P | U | F
T-5.4 | Drawings |  |  |  | Electrical |  | One‑line and riser diagrams of the normal electrical power and the emergency power distribution. Locate, size, and identify electrical, FMS & OIT Communications and Interface Systems as approved by the Electrical Engineer and RCDD FMS & OI&T Communications Design Professional(s). Show typical branch circuit wiring of offices, exam rooms, patient rooms, and lab areas. One-line electrical should show power distribution to MCR and each TR, including the branch circuit configuration for racks, cabinets, and supporting mechanical equipment in each space. |  |  | P | U | F
T.5.4.1 | Drawings |  |  |  |  | Bonding | Bonding plan for the site, building, telecommunications spaces, racks, and cabinets. Include unit bonding conductors, rack bonding busbars, rack bonding conductors, telecommunications bonding conductor, cable tray bonding conductors, primary bonding busbar, secondary bonding busbars, and connecting paths. Routing for bonding conductors should be shown in both plan and elevation views. |  |  | P | U | F
T.5.4.2 | Drawings |  |  |  |  | Power Chain | Show electrical distribution for IT equipment enclosures at the room and rack/cabinet level for the entrance rooms, MCR, and TRs. Distribution components such as busbars, taps, Zone PDUs, and Rack PDUs should be identified by salient characteristics. |  |  | P | U | F
T-5.5 | Drawings |  |  |  | Riser Diagrams |  | FMS Special Communications and OIT Communications TIP Riser Diagrams; ensure design does not have a single point of failure. Riser diagrams also need to show all systems interfaces. Telecommunications riser diagrams should include all telecommunications media, the associated pathways, the media specifications, media quantities and cable fiber counts from building entrance to all distribution spaces. Conduits or sleeves connecting stacked TRs should be detailed with size and quantity. See T-5-9 for drawing / CD requirements. |  |  | P | U | F
T-5.6 | Drawings |  |  | Site Plan |  |  | Site plan updated to show existing and proposed FMS, OIT and other telecommunications systems required by the project (insure the TIP does not have a single point of failure especially at the MCR). Site plan must include maintenance hole locations, vault locations and specifications, pedestals, monuments, conduit pathways, and pathway specifications. |  | P | U | U | F
T-5.7.1 | Drawings | [5 empty] | Identify all new FMS, Emergency, Safety, Medical, Disaster, OIT and other project approved telecommunications services to site and buildings, all new TIP fiber, copper, and coaxial cabling installations, all manholes and duct banks. |  |  | P | U | F
T-5.7.2 | Drawings | [5 empty] | Identify diversely routed distribution pathways between entrance rooms, MCR, and TRs for the campus. |  |  | P | U | F
T-5.8 | Drawings |  |  | Demolition Plans |  |  | Demolition plans shall Identify all telecommunications services and work required by the site (including existing to be retained) to be renovated. If an entire wing or area is demolished, provide reference note(s) to the architectural drawings. |  |  | P | U | F
T-5.9 | Drawings |  |  | Telecommunication Spaces |  |  | Provide 1/8” = 1’0” (1:100) scale floor plans that show typical telecommunications layouts for typical rooms. |  | P | U | U | F
T-5.10 | Drawings |  |  |  | Locations |  | Provision for all telecommunications spaces on the Telecommunications Drawings. TRs must stack vertically. |  | P | U | U | F
T-5.11 | Drawings |  |  |  | Locations |  | Provide locations for the Telephone Room, Entrance/DEMARC Rooms, Engineering Control, Police Control, Emergency Management Control and OSP Emergency Management Control (if not a part of the EMCR) Rooms on the Telecommunications Drawings. |  | P | U | U | F
T-5.12 | Drawings | [5 empty] | Ensure all telecommunications rooms, MCR, Antenna Head End and like areas (see minimums in T-5-11) do not have illegal obstructions present in and around (provide VA required EMI, RFI & EI filtering) each location, are sown on the Telecommunications Drawings, see T-5-9 for drawing / CD requirements. |  | P | U | U | F
T-5.13 | Drawings |  |  |  | Equipment |  | Identify all major FMS & OIT communications equipment and systems are drawn to scale. Ensure all means and OSHA clearances are met for installation, maintenance, servicing, removal and replacement of Telecommunications Equipment and Systems are, depicted and noted, on Telecommunications Drawings. |  | P | U | U | F
T-5.13.1 | Drawings | [5 empty] | Provide salient characteristic data on proposed racks, cabinets, and accessories including vertical exhaust ducts, inter-cabinet cable routing and grommets, and cable management accessories (ring and finger managers, radius bend assists, horizontal and vertical cable managers, et cetera). |  | P | U | U | F
T-5.13.2 | Drawings | [5 empty] | Provide drawing(s) and salient characteristics of structured cabling plant for the MCR (between MDAs and HDAs and between HDAs and server cabinets). Include media characteristics, quantities, and distances. |  | P | U | U | F
T-5.14 | Drawings | [5 empty] | Locate FMS & OI&T TIP cable locations. Locate all FMS & OI&T Communications Equipment and Systems are drawn to scale. Indicate FMS & OI&T Communications Equipment and Systems to be installed in the proposed Main Computer, Main Telephone, Telephone Operator’s, Telecommunications, Antenna Head End, Police Control, Engineering Control, Emergency Management Control and OSP Emergency Control (if not a part of the EMCR) Rooms are depicted and noted on the Telecommunication Drawings. Comply with TDM, EDM and OI&T DG. |  | P | U | U | F
T-5.15 | Drawings |  |  | Floor Plans |  |  | Provide floor plans including complete notes, legends, symbols list and details. Indicate room titles and area functions, location, and sizes of main computer, telephone room, and telecommunications rooms (ensure FMS and OIT systems are installed in the same room). Show locations of equipment, AC Power and Communications outlets, cable trays, regular and interconnecting conduits. |  |  | P | U | F
T-5.16 | Drawings |  |  | Construction Drawings |  |  | Provide telecommunication drawings stamped by certified RCCD professional. |  |  |  |  | F
T-5.17 | Drawings |  |  | Floor Plans |  |  | Drawings should show details of all end user devices and outlets. |  |  | P | U | F
T-5.18 | Drawings |  |  | Elevations |  |  | Show elevations of FMS, OIT Equipment, MCR and TRs to include back board elevations and interaction of mechanical, electrical, and telecommunications equipment. |  |  | P | U | F
T-5.18.1 | Drawings |  |  | Elevations |  |  | Provide elevation drawings for racks and cabinets showing equipment details (bonding and telecommunications terminations in rack and cabinet elevations including Equipment Distributors, Horizontal Distribution Areas, and Main Distribution Areas). Distribution components such as patch panels, fiber distribution cabinets, cassettes, and cable bundles should be identified by salient characteristics, including polarity. |  |  | P | U | F
T-5.19 | Drawings |  |  | Labeling Plan |  |  | Provide plans to properly label telecommunications spaces, equipment, electrical distribution, and telecommunications media. |  |  | P | U | F
T-5.20 | Drawings |  |  | CFD Analysis |  |  | Provide drawings from CFD analysis showing the operation of the MCR at commissioning and at ultimate design loading in all necessary normal and contingency operating states to show that the design is efficient and effective. |  |  | P | U | F
T-6.0 |  |  | ANTENNA REQUIREMENTS
T-6.1 | Report |  |  | Antenna |  |  | Ensure Antenna HE Room has properly sized roof or wall coax cable penetrations and roof or wall strengthening is in place to support required and additional radio antennas. |  | P | U | U | F
T-6.2 | Report | [5 empty] | Ensure external Antenna Farm Lightning Protection System is in place and connected to the Facility Lightning Protection System or a certified Earth Ground. |  | P | U | U | F
T-6.3 | Report |  |  | CCGS |  |  | Ensure internal Circulating Communications Ground System is in Place. |  |  |  | P | F
T-6.4 | Report |  |  | SMS-Security Management System |  |  | Ensure Security Management System is in Place. |  |  |  | P | F
T-7.0 |  |  | SPECIFICATIONS
T-7.1 | Report |  |  | CCGS |  |  | Show list of Specifications. |  |  | P
T-7.2 | Report |  |  | CCGS |  |  | Edit and mark-up Specifications. |  |  |  | P | F
VA SME
| Kelly Bates |  |  |  |  | Kelly.Bates@va.gov
| Forrest Frakes |  |  |  |  | Forrest.Frakes@va.gov

## Environmental Compliance
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME |  |  |  |  | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 |  |  |  |  | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments
|  | Environmental Compliance |  |  |  | VA submission requirements for Sustainability
EC-1.0 |  |  | BASIS OF DESIGN
EC-1.1 | Report |  |  | Goal |  | The A-E shall design the project to comply with all applicable Federal, State, and Local Environmental Protection Standards, Regulations and Requirements governing air quality, water quality, solid waste and hazardous waste. The A-E shall design the facility to comply with the most stringent applicable standards. Identify all environmental hazards, liabilities, and compliance matters. Identify how to reach such determinations and define approach to mitigating each one. Common areas to identify would be Asbestos Presence and/or Contamination, Lead Contamination, Lead Containing Materials and Building components, Hazardous Materials and/or Waste Storage, Polychlorinated Byphenyls (PCB) containing articles or spilled materials. Review existing facility environmental permits and build upon those permits to meet project requirements. Examples are Stormwater Pollution Prevention Plan, Spill Prevention Control and Countermeasures Plan, Hazardous Waste Generator Status. | P | U | U | U | F
EC-2.0 |  |  |  | Environmental Management Plan (EMP) |  | The purpose of the EMP is to present an overview of known or potential environmental issues, requirements, regulations and permits that must be considered and addressed during construction. Incorporate construction related objectives and targets from both CFM Environmental Staff and the facility's Green Environmental Management System Coordinators (GEMS) or Environmental staff into the EMP, as applicable. Include in the EMP measures for protecting natural and cultural resources, required reports, permits requirements, regulatory consultations and other measures to be taken.
EC-2.1 |  |  | Identification of Existing Conditions |  |  | The below reports shall identify existing conditions at the Site and shall be incorporated into the EMP.
EC-2.2 | Report | Asbestos Management Plan (AMP) |  |  |  | Review facility Asbestos Management Plan and incorporate Project to it. See VHA Directive 7714 for specific requirements. |  | P | U | F
EC-2.2.1. | Report |  | Develop Implementation Plan for AMP |  |  |  |  | P | U | F
EC-2.2.2 | Report |  | Baseline Testing and Calculations for volume of ACM |  |  | Assessment of compliance with 40 CFR 61, Subpart M |  | P | U | F
EC-2.2.3 | Report |  | Implementation of Design Specification 02 82 11 |  |  | Design Specification for Traditional Asbestos Abatement |  | P | U | F
EC-2.2.4 | Report |  | Implementation of Design Specification 02 82 13.13 |  |  | Design Specification for Glove bag Asbestos Abatement |  | P | U | F
EC-2.2.5 | Report |  | Implementation of Design Specification 02 82 13.19 |  |  | Design Specification for Asbestos Floor Tile and Mastic Abatement |  | P | U | F
EC-2.2.6 | Report |  | Implementation of Design Specification 02 82 13.21 |  |  | Design Specification for Asbestos Roofing Abatement |  | P | U | F
EC-2.2.7 | Report |  | Implementation of Design Specification 02 82 13.31 |  |  | Design Specification for Asbestos Transite Abatement |  | P | U | F
EC-2.2.8 | Report |  | Implementation of Design Specification 02 82 13.41 |  |  | Asbestos Abatement for Total Demolition Project |  | P | U | F
EC-2.3 | Report | Lead Contamination identification and management. | [5 empty] | P | U | F
EC-2.3.1 | Report |  | Implementation of Design Specification 02 83 33.13 |  |  | Lead-Based Paint Removal and Disposal |  | P | U | F
EC-2.4 | Report | Facility Hazardous Waste Management Plan |  |  |  | Incorporate applicable waste identification, characterization, and disposal based on the requirements of the facility as they are ultimately responsible for the handling of the waste. |  | P | U | F
EC-2.3.1 | Report |  | Regulated waste inventory and determination |  |  |  |  | P | U | U | F
EC-2.3.2 | Report |  | Proposed action plan for disposal |  |  | Include method of packaging and disposal as well as treatment standard to be used. Also, include training requirements needed for the removal, collection, packaging and transportation of the hazardous waste identified. |  | P | U | U | F
EC-2.4 | Report | Spill Prevention Control and Countermeasures Plan |  |  |  | Review existing plan and identity if equipment used during construction/demolition activities will need to be added to the inventory. Also, if inventory needs to be edited, additional training will be required. |  |  | P | U | F
E.C.-2.5 | Report | Environmental Permit Identification, Submissions and Plans |  |  |  | Review existing site environmental permits and required environmental permits necessary for project execution. Identify all permit, requirements, submissions, timeframe, agency coordination's and required submissions for permit application and approval. |  | P | U | U | F
E.C.-2.5.1 | Report |  | Permit Requirements Identification |  |  | The project may require that the government secure permits for pollution control, construction, operation, etc. As required, investigate the need for, report on, develop the required data and design information, and obtain and submit completed draft and final permit applications with supporting documentation to VA Facility and CFM Environmental Staff. Coordinate all contact with any applicable federal, state, and local regulatory agency through CFM and VA Facility Environmental Staff who will be responsible for submission of the application(s) for the final permit(s) where applicable. |  | P | U | U | F
E.C.-2.5.2 |  |  | Permits Requirements Report |  |  | Prepare a Permit Requirements Report which includes the following: a. Project Review Environmental Permit Checklist. b. Permitting authority (EPA, COE, state, local, etc.). c. Type of permit required (construction, operation, discharge, use, dump, dredge, fill, haul, etc.). d. Who is responsible for submitting the permit application. e. Procedure and time necessary to complete permit application and obtain permit. f. Permit fees required. g. Statement that the project is covered by variances or that the permit is not required. If a variance is required, describe the procedures on how it will be obtained. If a permit is not required, furnish reasons and supporting justification (cite state and local regulations). h. For each permit required, the A-E shall evaluate all applicable regulations to determine if monitoring devices are needed. Where required, monitoring devises shall be included in the project design. | P | U | U | U | F
E.C.-2.6. | Report | Historic Preservation and SHPO Section 106 Report |  |  |  | The following information shall be prepared by the A-E; a. Brief statement of work for the project. b. A detailed statement as to why replacement is proposed over repair. c. Whether the items being removed/replaced are original to the buildings/structures. If not, when were they installed? d. Dimensions (thickness, height, width), details, materials, and condition (dry rot, broken, etc..) of the items being repaired/replaced. e. One (1) set of 10% plans, specifications, and construction schedule. The AE and/or PM shall forward the submittals via the CFM Environmental Program for review and inclusion in the NEPA Implementation. |  | P | U | U | F
EC-2.5 | Report | National Environmental Policy Act Review, Implementation |  |  |  | The AE shall review, where available, the project NEPA documentation to ensure compliance with NEPA and previously executed NEPA documentation and impact analysis. For the current project the AE and PM shall engage OCFM Environmental Program to start the NEPA process and develop the Resource Avoidance Report. *Note This process shall be implemented with enough lead time to allow for the Environmental Program to develop a specific SOW, award a contract and execute the action. This will normally require a 6 month lead time. Results will be provided to AE and/or PM for their use in the design process. In situations where NEPA documentation is proceeding concurrent with the design effort, the AE shall provide design information, drawings and site information to CFM Environmental Staff and consultants in order to assist in the completion of NEPA documentation for the project. |  | P | U | U | F
EC-2.5.a | Drawings | Implementation of TEMPORARY ENVIRONMENTAL CONTROLS Specification 01-57-19 |  |  |  | The AE shall review the Temporary Environmental Control Specification 01-57-19 and or other Project/Site specific Environmental regulatory requirements, to ensure design documents meet the requirements of the specification and include any and all necessary environmental control requirements in the drawings and design package. |  | P | U | U | F
VA SME
| Fernando Fernandez |  |  |  | Fernando.Fernandez@va.gov
| Patrick Reed |  |  |  | Patrick.Read@va.gov

## Sustainability
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME |  |  |  |  | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 |  |  |  |  | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | SUSTAINABILITY |  |  |  | VA submission requirements for Sustainability
SU-1.0 |  |  | BASIS OF DESIGN
SU-1.1 | Report |  |  | Goal |  | Determine project sustainability goals and define how they will be accomplished with respect to siting, energy use reduction, potable water use reduction, sustainable materials, renewable energy, and protecting indoor environmental quality within a sustainable charrette. | P | U
SU-2.0 |  |  | Sustainability Plan
SU-2.1 | Report |  | Sustainability Report |  |  | Provide Sustainability Report with the following information: |  | P | U | U | F
SU-2.2 | Report |  |  | Baseline Requirements |  | Assessment of compliance with ASHRAE 90.1 baseline requirements. |  | P | U | U | F
SU-2.3 | Report |  |  | Narrative |  | Narrative highlighting design features incorporated to minimize the impact of climate change-related changes to local weather patterns or conditions. |  | P | U | U | F
SU-2.4 | Report |  |  | Daylighting |  | Narrative explaining strategy to incorporate daylighting into building design. Show daylit spaces over time during occupied hours using engineering grade 3D Model views for peak sun penetration during winter and summer. |  | P | U | U | F
SU-2.5 | Report |  |  | Summarize |  | Summarize/Update all energy reduction options considered, highlighting whether the options were adopted or rejected. Provide explanations for all options rejected. |  | P | U | U | F
SU-2.6 | Report |  |  | Renewable Energy |  | Summarize inclusion of renewable energy technologies in design. Include system sizing and energy output information at all subsequent phases. |  | P | U | U | F
SU-2.7 | Report |  |  | Heat Island |  | Summarize design features incorporated to reduce heat island effect. |  | P | U | U | F
SU-2.8 | Report |  |  | LEED or Green Globes |  | Summary of LEED or Green Globes credits being pursued and anticipated point levels to be achieved. |  | P | U | U | F
SU-2.9 | Report |  |  | Metered Systems |  | List of all systems being metered. |  | P | U | U | F
SU-2.10 | Report |  |  | Water-Use Reduction |  | Graphical representation (pie or bar chart) and description comparing various water-use reduction strategies to achieve the reduction goals and mandated water-use reduction requirements as part of the selected third-party rating system and VA sustainability guidelines. Coordinate the reporting with the results from the plumbing and site/civil storm water analysis to provide the potable water baseline and the required reduction target. Define strategies. |  | P | U | U | F
SU-2.11 | Report |  |  | Energy Consumption |  | Graphical comparison (pie or bar chart) and summary of the energy use intensity and energy consumption by end use for HVAC and lighting concepts evaluated as part of the SD1 phase. The summary should illustrate how the mandated energy conservation requirements, energy consumption and lighting design goals in VA design manuals and VA sustainability guidelines for the overall project are being achieved. Coordinate the reporting with the results from the energy and lighting analysis conducted as part of the mechanical and electrical/lighting systems evaluation. |  | P | U | U | F
SU-2.12 | Report |  |  | Indoor Environmental Quality (IEQ) |  | Graphical (pie or bar chart) and summary of the preliminary results and conclusions of the Indoor Environmental Quality (IEQ) impact of each of the HVAC concepts. In addition, provide a graphical representation of Green House Gas (GHG) emissions for the selected concepts as they relate to VA mandates. |  | P | U | U | F
SU-2.13 |  |  |  | Materials |  | Report of materials that contribute towards VA sustainability goals. |  | P | U | U | F
SU-2.14 | Report |  |  | Renewable Energy Capacity |  | Based on preliminary work provided in the Project Book, provide a summary and estimate of renewable energy capacity for the project as related to VA mandates and third-party certification requirements. Also, coordinate with the plumbing submission and submit as needed the explanation and technical backup information as to how the project shall meet the project goal for hot-water generation utilizing renewable solar energy. |  | P | U | U | F
SU-2.15 | Report |  |  | Cogeneration |  | If COGEN will be used, provide system description, expected electrical and heat output capacity, and lifecycle cost analysis |  | P | U | U | F
SU-2.16 | Report |  |  | Sustainable Certification |  | Documentation showing that project has been registered for either LEED or Green Globes certification. |  | P | U | U | F
SU-2.17 | Report |  |  | Alternative Transportation |  | Validate Project Book Alternative Transportation options supporting of VA Sustainable Design Manual considered, and selected. |  | P | U | U | F
SU-2.18 | Report |  |  | Compliance Validation |  | Per VA Sustainable Design Manual, provide draft "Guiding Principles Checklist, (Final checklist will be completed by VA Project Manager upon completion of LEED or Green Globes certification.) |  | P | U | U | F
SU-2.19 |  |  |  | LEED or Green Globes Rating |  | Submit and achieve Third Party sustainability rating. |  | P | U | U | F
SU-3.0 |  |  | CALCULATIONS
SU-3.1 | Calculations |  |  | Water Usage |  | Provide water use reduction calculations. Coordinate calculation submission for the potable water baseline and reduced consumption calculations with the plumbing engineer. Coordinate calculation submissions with the plumbing engineer to support the strategies to achieve the water reduction goals. |  |  | P | U | F
SU-3.2 | Calculations |  |  | Energy Analysis |  | Provide annual energy analyses for the purpose of optimizing the orientation and massing of buildings. |  |  | P | U | F
SU-3.3 | Calculations |  |  | Energy Modeling |  | Summarize/Update results of energy model and compliance with VA energy reduction goals. Provide name of energy modeling software used. Provide data inputs used, including all parameters and assumptions. |  |  | P | U | F
SU-3.4 | Calculations |  |  | Renewable Energy |  | Provide renewable energy calculations. Coordinate calculation submissions with the mechanical and electrical trades. Include lifecycle cost calculations. |  |  | P | U | F
VA SME
| James Symanski |  |  |  | James.Symanski@va.gov

## Historic
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 | [5 empty] | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | HISTORIC |  |  |  |  | VA submission requirements for Historic
H-1.0 |  | BASIS OF DESIGN |  |  |  |  | Submit the Basis of Design (BOD) report updated at each submittal with the following information:
H-1.1 | Report |  |  | Narrative |  |  | Narrative establishing project goals, and objectives for projects where it has been determined will occur on clearly identified historic resources or within a historic district. Initiate discussions with VA HP Office to determine potential adverse effects the project may have on documented historic resources. | P | U | U | U | F
H-1.2 | Report |  |  | Phasing |  |  | Provide analysis of implementation strategies, phasing, and sequencing considerations. Include analysis of necessary consultations required for historic properties. | P | U | U | U | F
H-1.3 | Report |  |  | Finish Schedule |  |  | Provide Room Finish Schedule in tabular format that identifies room number (both Design & Wayfinding), materials, and color selections for all exposed surfaces as required in H-2.1 as well as for interior spaces and materials identified as historic. (Coordinate with Architecture/Interior) Identify process for determining treatment of historic surfaces and their preservation. |  |  | P | U | F
H-1.4 | Report |  |  | Sample Boards |  |  | Provide material and finish sample boards. Provide final colors, finishes, furniture and fabrics, all keyed to floor plans for exterior and interior areas identified as historic only. |  |  | P | F
H-1.5 | Drawings |  |  | Communicating the Design Aesthetic |  |  | Provide rendered visualizations as noted in the VA BIM STANDARD pursuant to A.3.9 for exterior and interior areas identified as historic only. |  | P | U | F
H-2.0 |  | SPACE PLANNING
H-2.1 | Drawings |  |  | Zones |  |  | Provide a description of the tentative preservation zoning of interior/exterior spaces. Describe the locations of the each zone, focusing on efforts to maintain original spaces. For exterior and interior areas the identification of preservation zones will be by designations of priorities for protection. Architect will discuss with VA HP Office. |  | P | U | F
H-2.2 | Drawings |  |  | Swing Space/Design and Construction Phasing Plan (4D) |  |  | If swing space impacts Historic resources or sites, provide a 3D/4D communication plan for swing space and sequence of work. Indicate construction barriers/fences, proposed laydown space and operational logistics. Refer to the VA BIM STANDARD pursuant to A-3.10. | P | U | U | U | F
H-3.0 |  |  | ROOM DATA SHEETS |  |  |  | Electronic 2D PDFs (minimum scale 1/4" = 1"-0" (1:50) linked to the plan sets as per the requirements in the DDR for Historic designated spaces only. |  |  | P | U | F
H-3.1 | Drawings | [5 empty] | Minimum room dimensions and clearances. (Coordinate with Architecture). |  |  | P | U | F
H-3.2 | Drawings | [5 empty] | Door size and special requirements (fire rating, vision panel, finish hardware, access control, etc.)(Coordinate with Architecture/Interior). |  |  | P | U | F
H-3.3 | Drawings | [5 empty] | Wall types (fire ratings, shielding, acoustic, etc.). Coordinate with Architecture). |  |  | P | U | F
H-3.4 | Drawings | [5 empty] | Architectural casework configuration and location. (coordinate with Architecture/Interior). |  |  | P | U | F
H-3.5 | Drawings | [5 empty] | Room Finishes. (Coordinate with Interior). |  | P | U | U | F
H-4.0 |  |  | ARCHITECTURAL DRAWING DELIVERABLES |  |  |  | Follow the requirements in the DDR, the VA BIM STANDARD and as noted below for Historic designated spaces.
H-4.1 | Drawings |  |  | Title/Cover Sheet(s) |  |  | Cover Sheets: project name and address, VA project number, location map, signature block, name and address of VA, architect, engineers, and other consultants; Project Data with index of drawings, legend of abbreviations and symbols; Project Codes and Standards Sheet with a list and summary of the applicable project codes, applicable VA Standard Manuals and Guides by name and issuance date. |  | P | U | U | F
H-4.2 | Drawings |  |  | Site Plans |  |  | Provide a site plan indicating Historic designated spaces (min. 1"=30.0') indicating demolition, building location, parking, pedestrian and vehicular circulation, emergency vehicle access, loading docks, and all other major landforms and site features. (Coordinate with Civil Engineering discipline). |  | P | U | U | F
H-4.3 | Drawings |  |  | Demolition Plans |  |  | Demolition floor and ceiling plans for Historic designated areas to be renovated and areas below where work in space below is required (minimum 1/8"=1'-0" (1:100) with finish schedule and wall types. Coordinate with phasing plans, Interim Life Safety Measures (ILSM) and Infection Control Risk Assessment (ICRA). Describe compliance with VA FPDM Section 1.4. |  |  | P | U | F
H-4.4 | Drawings |  |  | Floor Plans |  |  | Provide floor plans showing departmental adjacencies, major circulation routes and layouts for each floor, including interstitial floors, showing internal organization of each department, vertical and horizontal circulation, location of mechanical and electrical equipment rooms, utility shafts, patient and staff entrance, receiving/shipping, and location of section cuts in all Historic designates spaces. (minimum scale 1/16” =1’-0” (1:200). Included column centerline and overall building dimensions. Coordinate with Civil Engineering discipline for finished floor of structures and flood zones. |  | P | U | U | F
H-4.5 | Drawings |  |  | Roof Plans |  |  | Provide 1/8"=1'-0" (1:100) scale roof plans depicting all roof features (drains, overflows, slopes, crickets, ridges, valleys, penetrations, equipment, davits, walk pads, etc.). Indicate all green roof types and areas impacting Historic designated spaces. |  |  | P | U | F
H-4.6 | Drawings |  |  | Exterior Elevations |  |  | For Historic designated spaces, provide building elevations at a minimum of 1/16"=1'-0" (1:200) with fenestration, penthouses, materials, finish floor elevations, floor-to-floor heights, overall building height, window and louver types, entrances, canopies, skylights, and adjacent grades. Include separate elevations indicating base building with expansion shown on floor plans. Provide building elevations of complex areas at a minimum scale of 1/4"=1'-0" (1:50). |  | P | U | U | F
H-4.7 | Drawings |  |  |  | Building Sections |  | For Historic designated spaces, provide building sections at minimum scale 1/16"=1'-0" (1:200) through major portions of building. |  | P | U | U | F
H-4.8 | Drawings |  |  |  | Wall Sections |  | For Historic designated spaces, provide wall sections indicating floor-to-floor heights, overall building heights, materials, fenestrations, and assemblies. |  |  |  | P | F
H-4.9 | Drawings |  |  |  | Wall Types |  | For Historic designated spaces, provide each wall type at minimum scale of 1"=1'-0" (1:10). Indicate sound attenuation and fire ratings. Identify UL or other acceptable testing agency design number. |  |  |  | P | F
H-4.10 | Drawings |  |  | Construction Details |  |  | Construction details at scale large enough to clearly show components and assembly: windows, storefront, waterproofing, roof accessories, equipment mounting and suspension shielding, etc. For Historic designated spaces, provide 3D PDF details for all complex roof/wall/window interfaces and include in electronic 2D drawing sets. |  |  |  | P | F
H-4.11 | Drawings |  |  | Vertical Transit Plans & Details |  |  | Vertical transit details for stairs, elevators, lifts, dumbwaiters, linen and trash chutes, and pneumatic tube stations. For Historic designated spaces, provide plans at minimum scale of 1/4"=1'-0" (1:50), sections and details at scale large enough to convey design intent. |  |  |  | P | F
H-4.12 | Drawings |  |  | Door Schedules |  |  | Door schedule with door and frame details, threshold details, door number, door and frame types, dimensions, ratings, materials, glazing, security requirements, and finish hardware. (coordinate with Architecture). |  |  |  | P | F
H-4.13 | Drawings |  |  | Door Types |  |  | For Historic designated spaces, provide graphical depiction of each door type. (Coordinate with Architecture). |  |  |  | P | F
H-4.14 | Drawings |  |  | Interior Elevations |  |  | For Historic designated spaces, provide interior elevations at minimum scale of 1/4"=1'-0" (1:50) showing medical gases, power, data, communications, millwork, architectural casework, equipment and other built-in items. Identify PRC items by JSN and as noted in the VA BIM STANDARD. (Coordinate with Architecture) |  |  |  | P | F
VA SME
| Hector Abreu |  |  |  |  | Hector.Abreu@va.gov

## Physical Security
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME |  |  |  |  | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 |  |  |  |  | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | PHYSICAL SECURITY |  |  |  | VA submission requirements for Physical Security
PS-1.0 |  |  | BASIS OF DESIGN
PS-1.1 | Report |  |  | Narrative |  | Basis of Design (BOD) including the physical security requirements and a report including verification that a qualified Security Specialist and Structural Blast Specialist shall be retained by the A/E. The conceptual design shall address the physical security requirements as defined in VA Physical Security Design Manual. Create subsections corresponding to each of the chapters of the Physical Security standard, (i.e., Site Considerations, Building Entrances and Exits, Functional Areas, and Building Envelope). | P | U | U | U | F
PS-1.2 | Report |  |  | Designations of Facilities (Mission Critical, Life-Safety Protected w/ Mission Critical Util/Sys Redundancies, or Life-Safety Protected) |  | Determination of facility designation and the corresponding requirements. Obtain approval from Authority-having-Jurisdiction per PSDM, in writing to any exception to the Physical Security Design Manual (PSDM). | F
PS-1.3 | Report |  |  | Telecommunications |  | Address Telecommunications System and Areas’ security requirements that must conform to approved standards and specifications. | F
PS-1.4 | Report |  |  |  |  | Identify Telecommunications Areas to be addressed to including PACS Police Service control and management of all Spectrum Management OI&T physical spaces. | P | U | U | F
PS-1.5 | Report |  |  |  |  | Assess Concept assessments including applicable Crime Prevention through Environmental Design (CPTED) principles. | P | F
PS-1.6 | Report |  |  | Requirements |  | Describe physical security requirements and an overview of provisions to be implemented including setbacks, building envelope, structural system, monitoring, intrusion detection, and other systems that must be considered. Include special construction requirements such as lead, electromagnetic, and RF shielding, pneumatic tube systems, automated materials handling systems, security requirements for pharmacy, designated COOP facilities, and Security Operations Center. |  | P | U | U | F
PS-1.7 | Report |  |  |  |  | Include Project Book information to identify and locate primary and backup utility sources for water, power, emergency power, fuel, communications, and sewer. |  | F
PS-1.8 | Report |  |  |  |  | Coordinate security requirements on room data sheets. |  | P | U | F
PS-1.9 | Report |  |  |  |  | Provide connection matrix for security devices. |  |  |  | P | F
PS-1.10 | Report |  |  |  |  | Provide catalog cut sheets for proposed security equipment: CCTV, monitors, access control systems, PACS, and screening equipment. |  |  |  | P | F
PS-1.11 | Report |  |  | Quality Control |  | Provide letter from the security specialists, affirming that they have performed a back-check to confirm that all the physical security elements have been incorporated into the Construction Documents. |  |  |  |  | F
PS-1.12 | Report |  | FINAL REPORT | [7 empty] | F
PS-2.0 |  |  | CALCULATIONS
PS-2.1 | Calculations |  |  | Dynamic Analyses |  | Provide blast-loading, environment and dynamic analyses, of typical glazing, exterior envelope elements, vulnerable interior, and exterior structure. |  |  |  | P | F
PS-3.0 |  |  | DRAWINGS and MODELS |  |  | As per the VA BIM STANDARD and below
PS-3.1 | Drawings |  |  | Site Plans |  | Provide Site Plan (1"=100.0') scale showing:
PS-3.2 | Drawings |  |  |  |  | Perimeter fence (Coordinate with Civil Engineer). |  |  | P | F
PS-3.3 | Drawings |  |  |  |  | Perimeter fence with pedestrian access points (Coordinate with Civil Engineer). |  |  | P | F
PS-3.4 | Drawings |  |  |  |  | Location of vehicle access points - private, public, commercial (Coordinate with Civil Engineer). |  |  | P | F
PS-3.5 | Drawings |  |  |  |  | Type of access control procedures and devices. |  |  | P | F
PS-3.6 | Drawings |  |  |  |  | Location of active and passive barriers (Coordinate with Civil Engineer). |  |  | P | F
PS-3.7 | Drawings |  |  |  |  | Vehicular circulation and parking (Coordinate with Civil Engineer). |  |  | P | F
PS-3.8 | Drawings |  |  |  |  | Site lighting (Coordinate with Electrical Engineer). |  |  | P | F
PS-3.9 | Drawings |  |  |  |  | Guard stations, vehicle barriers, inspection facilities, and vehicle stacking areas (Coordinate with Civil and Electrical Engineer). |  |  | P | F
PS-3.10 | Drawings |  |  |  |  | Camera locations (Coordinate with telecommunications and electrical disciplines). |  |  | P | F
PS-3.11 | Drawings |  |  | Security Camera Sightlines |  | Review security camera sight lines with location of landscape features and proposed mature vegetation (Coordinate with Landscape Architect). |  |  |  | P | F
PS-3.12 | Drawings |  |  |  |  | Crime Prevention Thru Environmental Design (CPTED) implementation plan. |  |  |  | P | F
PS-3.13 | Drawings |  |  | Floor Plans |  | Coordinate with architectural and engineering requirements for the following:
PS-3.14 | Drawings |  |  |  |  | Provide coordinated drawings of public entrances, lobbies, staff and service entrances, emergency management and security operations and control center. |  |  | P | F
PS-3.15 | Drawings |  |  |  |  | Agent cashier, cache, child care center, main computer room, COOP site, Emergency Department, emergency generator room, central energy plant, loading dock and service entrances, mail room, pharmacy, research laboratories, and vivarium. |  |  | P | F
PS-3.16 | Drawings |  |  | Physical Security Plan |  | Provide physical security plan showing location of security cameras, card readers, and screening equipment at a minimum scale 1/8"=1'-0" (1:100). |  |  | P | U | F
PS-3.17 | Drawings |  |  | 3D Panoramic Visualization |  | Using the Model, provide 3D visualization of interior security camera views. |  |  |  | P | F
VA SME
| Fred Lau |  |  |  | fred.lau@va.gov

## Elevator-Transport
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME |  |  |  |  | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 |  |  |  |  | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  | Description | Proj. Book | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments / Location
|  | ELEVATOR AND LOGISTICS |  |  |  | VA submission requirements for Elevator and Logistics
EL-0 |  |  | REFERENCE |  |  | The individual disciplines will use initials for identity: Vertical Transport - VT, Materials Management - MM, Waste Management - WM, Sterile Processing Services - SPS, Materials Handling - MH. When referencing the combination of these services as a coordinated and integrated support service it shall be referred to as: Logistics.
EL-1.0 |  |  | BASIS OF DESIGN |  |  | As a minimum, refer to and comply with all requirements noted in PG-18-3T18, PG18-10 and all Other VA Design standards including PG18-12 Chapters 284: Logistics Services and 285: Sterile Processing Service and Nutrition and Food Services (PG18-9 Chapter 224) and Environmental Management Service Laundry And Linen Operation (PG18-9 Chapter 408).
EL-1.01 | Report |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling - Logistics Report(s). |  |  | Provide studies, analysis (showing calculations) and reports on the Support Service requirements for all facilities to be serviced whether they are part of the Project in question or on the campus or not. Determine the adequacy or inadequacy of planned and existing support elements to support all of the functions and departments they are to serve. Determine the ROM space / costs for adding, expanding, enhancing, reducing or otherwise changing the combination of new and existing conditions to ensure proper MM / WM / VT / MH / SPS / Logistics support is available to the total of the combined facilities served whether on or off the local campus. | F | P | U | U | U | F
El-1.02 | Data Report |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling - Logistics. Data Report. |  |  | Provide Data Report that will be used as the basis for the Transport / Logistics studies and recommendations. | F | P | U | F
EL-1.1 | Transport / Logistics Studies and Report |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Provide project type / size appropriate studies, analysis and reports (TLA / ETSA / MMA / WMA / MH) as noted and directed in PG18-3 Topic 18 and standards referenced therein. This includes all traffic studies, Life Cycle Cost Analysis, etc. Reports to be fully updated for each design phase to ensure it remains current with the designs, traffic, operational and physical aspects of the project throughout the design process. Designs and project narratives shall conversely be updated to reflect the contents and recommendations in the updated reports. Final Submittals to be used for the Basis of Design during the CA Phase. | P | P | U | U | U | F
EL-1.1.1 | Study and Report - Waiver |  | Space for Materials Handling Systems (i.e., AGVS, AMR, PTS, etc.) |  |  | Where a MM, WM, VT, SPS, MH or Logistics system is justified and recommended in a TLA / ETSA / MMA / WMA report, the departments, functions, rooms, adjacencies etc. required for that system but not addressed or properly represented in the VA PG-9's: Space Planning Criteria; shall be immediately identified, quantified and reported. Examples would be: specialized maintenance areas; space reductions from higher efficiencies; etc. A written waiver request for the deviation / change shall be submitted immediately with a copy of all waiver requests attached within an appendix to the design phase (updated) report such as a TLA or MMA. The VA's response to the waiver request shall be added to the appendix to the report to memorialize the response. | P | P | U | U | F
EL-1.1.2 | Study and Report - Coordination |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | The Transport / Logistics Consultant shall become familiar with the submittal requirements noted in PG18-15 for all disciplines and provide the data needed to Other disciplines in a timely manner to advance the project with minimum delays and redesigns. This includes attention to "special" systems such as PTS, AGV, Trash/Linen Chutes, etc. where they are not "standard" equipment and their design requirements may not be familiar to Other disciplines. Pay special attention to conflict resolution for PTS and AGVS and interfaces to fire / smoke alarm systems. | P | P | U | U | U | F
EL-1.1.3 | Study and Report - Nutrition and Food Service Coordination |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling - Logistics coordination with Nutrition and Food Service. |  |  | Where the Transport / Logistics Consultant (TLC) is not providing the Studies and Designs for Nutrition and Food Services (NFS), Patient and Non-Patient, it shall be generally understood that the activities within the NFS departments shall be studied / designed / specified by the specialized NFS designer. The MM / WM / VT / MH functions supporting NFS but outside of the department perimeters, including clean and soiled truck docks and transport, shall be the responsibility of the TLC using the criteria, data, product volume and Other relevant information supplied by the NFS designer. Where automation such as AGVS, AMR, VT and Pneumatic Systems are used these are to be designed into the NFS operations by the TLC with the close cooperation of the Other applicable designers including the NFS designer. | P | P | U | U | U | F
EL-1.13 | Special - Technology Reports and Documents |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | It is recognized that the Transport and Logistics industries, along with Others, are undergoing rapid, major and significant technological changes that may be unknown to non-experts in these fields. The consultant shall issue special reports / white papers in a timely manner where new and technologically advanced equipment / systems are being planned and specified that has impacts on the planning of Other designer disciplines. | P | P | U | U | U | F
EL-1.1.4 | Report |  | Seismic Retrofit Projects (Seismic EQ funded) |  |  | Analyze impact of seismic correction plan on automatic transport system. Determine minimal acceptable changes necessary to implement seismic corrections. | P |  | P | U | F
EL-2.0 |  |  | CALCULATIONS |  |  | Per PG18-10 and PG18-3 Topic 18
EL-2.1 | Calculations |  |  |  |  | Submit calculations as required in PG18-10 and PG18-3t18.for all studies. Calculations are to show the input information and relevant outcomes. | P | P | U | U | U | F
EL-3.0 |  |  | DRAWINGS and MODELS |  |  | As per the VA BIM STANDARD and PG18-10 AND PG18-3t18
EL-3.1 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Submit overall floor plans at a minimum of 1/16”=1’-0” (1:200) indicating location of proposed and existing MM / WM / VT / MH / SPS / Logistics devices and systems. Indicate proposed routes and non-scaled "riser diagram" sketches for automatic transport systems. |  | P | U | U | U | F
EL-3.2 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Floor plans at a minimum of 1/8”=1’-0” (1:100) drawings of the MM / WM / VT / MH / SPS / Logistics systems and devices. Indicate devices including but not limited to: processing and storage equipment, MH devices, door interfaces, tracking, piping, battery charging areas, blower rooms, queuing areas, cart holding areas, cart washer, central control area, maintenance areas and floor and/or wall and/or overhead mounted or recessed control units. Indicate architectural and utility elements to be used for these systems. |  | P | U | U | U | F
EL-3.3 | Drawings |  | Pneumatic Tube and Chute Systems: |  |  | Show station locations recommended in the PG18-3t18 studies and accepted. Develop and coordinate the horizontal / vertical (including shaft ways) routing for pneumatic systems so that there are early and continuous efforts to avoid conflicts with the building, structures, departments and utilities without compromising the related system operations. Provide weights and reactions where necessary. |  | P | U | U | U | F
EL-3.4 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Provide separate drawings for major MM / WM / VT / MH / SPS / Logistics systems and equipment. As a minimum provide: dimensioned H x D x W equipment drawings, show installation space requirements including necessary maintenance clearances, details of required utilities and ventilation, provide details of corridors for automated / manual transport systems showing pathways and clearances, show VT equipment locations and details, show dimensions and details for carts to be used by automated and semi-automated systems, MM / SPS storage equipment, dock equipment, PTS stations and equipment, tube routings, processing equipment, shaftways, battery chargers, hoistway enclosures, pits, cabs, machine and blower room access and railings, and entrances using larger scale than floor plans as necessary. Show dimensional locations of equipment and devices. |  |  | P | U | U | F
EL-3.5 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. - Fire Protection |  |  | Coordinate proactively with the Fire Protection specialists, information on the various fire protection features and devices required for the various systems including interface to the fire / smoke system. Develop and provide fire door interfaces to relevant systems such as AGVS / AMR. Develop strategies and methodologies for all automated and semi-automated systems for compliance to all Fire Protection codes and standards. For example: Clearing obstructions from AGVS / AMR system transporter / carts from egress routes, doors and corridors; system activities where operations occur in multiple zones; etc. |  | P | U | U | U | F
EL-3.6 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Locate machine and equipment rooms for MM / WM / VT / MH / SPS / Logistics systems including: elevators, cart lifts, dumbwaiters, Pneumatic Chute Systems, PTS and AGV systems, mechanical / utility spaces. Indicate minimum dimensions, ventilation, structural and power requirements. |  | P | U | U | U | F
EL-3.7 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Provide details of elevator and other transport equipment at scales large enough to describe construction and installation requirements. Indicate size and locations of trap doors, hoist beams, divider beams, PTS blowers / diverters / exchangers, AGVS / AMR battery chargers, Pneumatic Chute diverters / turbines and similar equipment for people and materials transport systems. |  |  | P | U | U | F
EL-3.8 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Coordinate with Structural Engineer and provide size of machine beams and end reactions. Indicate location and detail of machine beam pockets. Show rail loadings and hydraulic elevator piston pit loads. |  |  | P | U | U | F
EL-4.0 |  |  | SPECIFICATIONS AND NARRATIVES
EL-3.09 | Preliminary Specifications |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Submit, as an attachment to the ETSA; MMA; WMA or TLA report an example of the specifications for major equipment / systems that are intended for use on the Project. Use current standard VA specifications where they are available and submit for approval, in the SD1 phase: the Consultant's proven successful current specification(s) when a current DVA specification is not available. |  |  | P | U
EL-3.10 | Interim Specifications |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Submit, generic outline specifications describing the important characteristics and features that contains the headings for every section intended for the final specification. A separate section of the specifications shall include the detailed traffic matrix developed for automated systems such as an AGVS / AMR or PTS. |  |  |  | P | U
EL-3.10 | Specifications |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Submit the final generic specifications that are created for high quality installations at competitive costs. Specifications shall be a combination of hardware / functional requirements to ensure that important functions can be achieved by qualified suppliers using different hardware / software without eliminating or compromising the intended functions / operations. A separate section of the specifications shall include the traffic matrix developed for automated systems such as an AGVS / AMR or PTS. |  |  |  |  | P | F
|  | AUTOMATIC GUIDED VEHICLES |  |  |  | VA submission requirements for Automatic Guided Vehicles (AGV)
AG 1.0 |  |  | NOTE 1: |  |  | For projects involving Automatic Guided Vehicles, please refer to VA Topic 18-1 AGV and AMR Submittal Schedule.
|  | PNUMATIC TUBES |  |  |  | VA submission requirements for Pnumatic Tube Systemd
PT 1.0 |  |  | NOTE 1: |  |  | For projects involving Pnumatic Tube Systems, please refer to VA Topic 18-1 AGV and AMR Submittal Schedule.
VA SME
Brian Phillips |  |  |  | Brian.Phillips@va.gov

## Cost Estimating
PG 18-15 Spreadsheet v2.0
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME | [5 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
0 | [5 empty] | 0 | 2020-11-01
Submittal Checklist
Seq. No. | Type | Topic |  |  |  |  | Description | CONCEPT | SD1 | SD2 | DD | CD | Submitted | Pending | N/A | Comments
|  | COST ESTIMATING |  |  |  |  | VA submission requirements for Cost Estimating
CE-1.0 |  |  | ALTERNATIVES
CE-1.1 | Report |  |  | Concept Evaluation Summary Report |  |  | A comparison table showing costs for all concepts. Costs shall be broken down into project elements or phases to facilitate comparison of one concept to another. | F
CE-1.2 | Report |  |  | Value Management Report |  |  | Submit a summary of alternatives developed during the Value Management workshop and proposed actions for each, as per current CFM Value Management Policy & SOP. | P | U | U | F
CE-2.0 |  |  | ESTIMATE
CE-2.1 | Report |  |  | UNIFORMAT II Level 2 Estimate |  |  | Prepare order of magnitude cost estimate for each concept – UNIFORMAT II Level 2 estimate. Include the following in the Preliminary estimate and each Updated estimate thereafter, per the below requirements: Cost Model, Budget Tracking, Separate Computations, Project Data Sheets, Market Survey. | P | U | U
CE-2.2 | Report |  |  | UNIFORMAT II Level 4 Estimate |  |  | UNIFORMAT II Level 4 estimate with Level 3 summary. Provide Level 4 & 5 detail for components that have been sufficiently defined in the drawings & specs to be quantifiable at that level. Final WBS II Level 4 Cost Estimate incorporating all changes to CD1 documents. Include the following in the Updated estimate and the Final estimate, per the below requirements: Cost Model, Budget Tracking, Separate Computations, Project Data Sheets, Market Survey. |  |  |  | U | F
CE-2.3 | Report |  |  | Prepare estimate in the Construction Specification Institute (CSI) 50 Division Master Format |  |  | Estimate Format Compatible with Construction Industry Format * |  |  |  | U | F
CE-2.4 | Report |  |  |  | Cost Model |  | Cost model based on project limitation of construction cost (cost target for construction). |  | P | U | U | F
CE-2.5 | Report |  |  |  | Budget Tracking |  | Budget tracking by phase. |  | P | U | U | F
CE-2.6 | Report |  |  |  | Separate Computations |  | Separate computations for site, each building, new work, renovations, and alternates. |  | P | U | U | F
CE-2.7 | Report |  |  |  | Project Data Sheets |  | Project Data Sheets (refer to VA cost estimating guidelines). | P | U | U | U | F
CE-2.8 | Report |  |  |  | Market Survey |  | Provide Market Survey. |  | P | U | U | F
CE-2.9 | Report |  | FINAL REPORT |  |  |  | Written responses to review comments from previous submission. All previously submitted documents updated to reflect review comments. |  | P | U | U | F
VA SME
| Eric Hoover |  |  |  |  | J.Eric.Hoover@va.gov