## Room Data Sheets
ROOM DATA SHEETS - 11/01/2023 | ROOM CODE | ROOM NAME | Indoor Temperature Cooling F | Indoor Temperature Cooling C | Indoor Temperature Heating F | Indoor Temperature Heating C | Indoor Relative Humidity % RH MAX | Indoor Relative Humidity % RH MIN | Minimum Total ACH | Minimum OA ACH | Room Air Return Exhaust G Exhaust S | Maximum Noise Level NC | Room Air Balance | Individual Room Control Temp | Individual Room Control Flow | Unoccupied ACH | Note 1 | Note 2 | Note 3 | Note 4 | Note 5 | Note 6 | Note 7
AUTOPSY SUITE | [16 empty] | General: The room names listed are from the VA PG 18-9 Chapter 240 Revised October 3, 2016. The actual room layouts, equipment disposition, and the HVAC parameters may vary with the project scope of work.
AUTOPSY SUITE | LBAR1 | Autopsy Room | 75 | 24 | 68 | 20 | 60 | 30 | 12 | 12 | Exhaust (S) | 40 | ( - ) | Yes | CV |  | Note 1 - Air Distribution. Locate exhaust air intakes at the ceiling and floor level. Locate the floor level inlets approximately 7 in [175 mm] above the floor. | Note 2 - Canopy Hood. A canopy hood may be required over the dissecting tables to capture exhaust at the maximum rate of 100 fpm [0.5 m/s] through the hood face area. Coordinate the exhaust air volume and exhaust location with the manufacturer of the dissecting tables. | Note 3 - Room Noise Level. Noise level lower than NC 35 may be required where audio/video recording is performed. | Note 4 - Occupied and Unoccupied Modes. Evaluate the feasibility of providing occupied/unoccupied modes based on anticipated usage of these spaces.
AUTOPSY SUITE | LBTS1 | Gross Specimen Storage Room | 75 | 24 | 68 | 20 | 60 | 30 | 6 | 6 | Exhaust (S) | 40 | ( - ) | Yes | CV |  | Note 1 - Air Distribution. Coordinate location of the exhaust air inlet over the sink and counter area to capture the exhaust air fumes.
Biomedical Laboratory Research & Development (BLR&D) | SB173 | BLR&D Female Staff Shower, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Biomedical Laboratory Research & Development (BLR&D) | SB184 | BLR&D Male Staff Shower, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Biomedical Laboratory Research & Development (BLR&D) | SB202 | BLR&D Female Staff Toilet, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Biomedical Laboratory Research & Development (BLR&D) | SB203 | BLR&D Male Staff Toilet, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Biomedical Laboratory Research & Development (BLR&D) | SB244 | BLR&D Housekeeping Aides Closet (HAC), Bldg Sprt | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV
Biomedical Laboratory Research & Development (BLR&D) | SB653 | BLR&D Mailroom, Lgstcs Scv | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Biomedical Laboratory Research & Development (BLR&D) | SB773 | BLR&D Conference / Multipurpose Room, Lgstcs Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
Biomedical Laboratory Research & Development (BLR&D) | SC701 | BLR&D Lab Access / Protocol Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | CV |  | Note 1 - Supply Air Volume. Increase the supply air volume, as required, to meet the transfer air demands of the adjoining spaces, such as, toilets, janitor closets, soiled utility rooms, laboratories, spaces requiring negative air balance, and exterior doors requiring ex-filtration.
Biomedical Laboratory Research & Development (BLR&D) | SC702 | BLR&D Bench Unit, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained. | Note 2 - Room air can be returned only if chemicals are not used in the room.
Biomedical Laboratory Research & Development (BLR&D) | SC703 | BLR&D Ghost Corridor. R&D | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained. | Note 2 - Room air can be returned only if chemicals are not used in the room.
Biomedical Laboratory Research & Development (BLR&D) | SC704 | BLR&D Bench Support, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained. | Note 2 - Room air can be returned only if chemicals are not used in the room.
Biomedical Laboratory Research & Development (BLR&D) | SC711 | BLR&D Core Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
Biomedical Laboratory Research & Development (BLR&D) | SC712 | BLR&D Microscopy Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained. | Provide vibration control to prevent interfering with the electron microscope.
Biomedical Laboratory Research & Development (BLR&D) | SC713 | BLR&D Glassware Washing / Sterilization Room, R&D | NA | NA | NA | NA | NA | NA | 10 | 2 | Exhaust (S) | 40 | (-) | No | CV |  | Note 1 - Wet Exhaust System. Provide a wet exhaust system.
Biomedical Laboratory Research & Development (BLR&D) | SC714 | BLR&D Walk-in Refrigerator / Cold Room, R&D | 86 | 30 | 40 | 5 | NA | NA | 6 | NA | Return | 45 | (o) | Yes | CV |  | Note 1 - High Humidity Locations. (a) General. Provide a dedicated mechanical cooling unit, complete chilled water or direct-expansion (DX) coil and minimum MERV 7 filters. Provide minimum outdoor air per ASHRAE Standard 15 (latest edition) and capability to operate at 100% outdoor air during emergency refrigerant evacuation mode. Provide a variable speed drive to facilitate system operation in the normal and emergency modes. (b) Capacity - Mechanical Cooling Unit. Base the capacity on the maximum of: Internal heat gain (note that the heat dissipated by open chillers is much higher than hermetic chillers) Exhaust air volume required to dilute the refrigerant spill - see ASHRAE Standard 15 - 2016 or latest approved version. | Note 2 - All Other Locations. Provide a refrigerant leak detection system complete with field-installed refrigerant detection sensors, wiring and local control panel per ASHRAE Standard 15 - 2016 or latest approved edition. Provide an open protocol BACnet interface with the building ECC system. Provide local alarms per ASHRAE Standard 15 - 2016 or latest approved edition requirements. Provide remote alarms at the ECC. | Note 3 - Emergency Refrigerant Leak Evacuation System. Provide a refrigerant leak detection system complete with field-installed refrigerant detection sensors, wiring and local control panel per ASHRAE Standard 15 - 2016 or latest approved edition. Provide an open protocol BACnet interface with the building ECC system. Provide local alarm requirements per ASHRAE Standard 15 -2016 or latest approved edition. Provide remote alarms at the ECC. | Note 4 - Emergency Exhaust System. Upon activation by the leak detection system, the room air shall be exhausted outdoors by an emergency exhaust system and supply air system shall operate in 100% outdoor air mode. Provide exhaust air inlets in accordance with the recommendations of ASHRAE Standard 15 - 2016 or latest approved edition and chiller manufacturer. Activation of the leak detection system shall also trigger local and remote alarms. Provide emergency power for the emergency exhaust and supply fans and associated controls.
Biomedical Laboratory Research & Development (BLR&D) | SC715 | BLR&D Research Informatics Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Ventilation. Total ACH based on cooling load and HVAC equipment capacity, outside air per ASHRAE 62.1 -2016 or latest approved edition and provide as indicated in the air handling unit data sheet.
Biomedical Laboratory Research & Development (BLR&D) | SC716 | BLR&D General Storage Room, R&D | NA | NA | NA | NA | NA | NA | 4 | NA | Return | 40 | (+) | No | CV |  | Note 1 - HVAC Treatment. (a) For a small, 100 sf [9 m2] and smaller, unoccupied room, individual room temperature control is not required. Room can be supplied from any adjoining constant- volume air terminal unit serving similar interior or perimeter space. Ducted return air pick-up is also not required, as the room air can ex-filtrate into adjoining spaces, such as, a non-exit corridor (NFPA 90A). (b) Individual room temperature control is required for a large, more than 100 sf [9 m2], occupied room. Provide a minimum of 2 ACH outdoor air. | Note 2 Sterile Storage See requirement for SRS05. Sterile Durables Storage in the Sterile Processing Service Room Data Sheets (RDS).
Biomedical Laboratory Research & Development (BLR&D) | SC717 | BLR&D Equipment Room, R&D | NA | NA | NA | NA | NA | NA | 4 | 4 | Exhaust (G) | 40 | (o) | No | CV |  | Note 1 - Room Supply. Air Provide a ducted, supply air takeoff from an adjoining air terminal unit.
Biomedical Laboratory Research & Development (BLR&D) | SC718 | BLR&D Service Core, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | CV |  | Note 1 - Supply Air Volume. Increase the supply air volume, as required, to meet the transfer air demands of the adjoining spaces, such as, toilets, janitor closets, soiled utility rooms, laboratories, spaces requiring negative air balance, and exterior doors requiring ex-filtration.
Biomedical Laboratory Research & Development (BLR&D) | SC719 | BLR&D Darkroom, R&D | 72 | 22 | 72 | 22 | 60 | 45 | 6 | 6 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Exhaust Duct. Provide acid-resistant exhaust duct if chemicals are used for film processing. | Note 2 - Plumbing. Evaluate the use of silver recovery plumbing, if required.
Biomedical Laboratory Research & Development (BLR&D) | SC721 | BLR&D Tissue Culture Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
Biomedical Laboratory Research & Development (BLR&D) | SC722 | BLR&D Isotope Room, R&D | 72 | 22 | 72 | 22 | 55 | 40 | 15 | 15 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Fume Hood Exhaust. Provide a dedicated exhaust system for the fume hood.
Biomedical Laboratory Research & Development (BLR&D) | SC723 | BLR&D Isotope Work and Storage Room, R&D | 72 | 22 | 72 | 22 | 55 | 40 | 15 | 15 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Fume Hood Exhaust. Provide a dedicated exhaust system for the fume hood. | Note 2 - Provide HEPA filtered exhaust if required by Safety Officer
Biomedical Laboratory Research & Development (BLR&D) | SC724 | BLR&D Flow Cytometry, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
Biomedical Laboratory Research & Development (BLR&D) | SC725 | BLR&D Fume Hood Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
Biomedical Laboratory Research & Development (BLR&D) | SS101 | BLR&D Conference / Multipurpose Room, Educ Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
Biomedical Laboratory Research & Development (BLR&D) | SS204 | BLR&D PI Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
Biomedical Laboratory Research & Development (BLR&D) | SS211 | BLR&D Touch-Down Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Biomedical Laboratory Research & Development (BLR&D) | SS212 | BLR&D Collaboration Station, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
Biomedical Laboratory Research & Development (BLR&D) | SS218 | BLR&D Research Associate Workstation, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Biomedical Laboratory Research & Development (BLR&D) | SS224 | BLR&D Private Call Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
Biomedical Laboratory Research & Development (BLR&D) | SS232 | BLR&D Female Staff Locker Room, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Biomedical Laboratory Research & Development (BLR&D) | SS241 | BLR&D Male Staff Locker Room, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Biomedical Laboratory Research & Development (BLR&D) | SS262 | BLR&D Staff Breakroom, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air. Return air is permitted if the lounge is not equipped with vending machines, microwave, refrigerator, etc., otherwise follow requirements in ASHRAE Standard 62.1 - 2016 or latest approved edition.
Biomedical Laboratory Research & Development (BLR&D) | SS268 | BLR&D Copy / Supply Alcove, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
Biomedical Laboratory Research & Development (BLR&D) | SS285 | BLR&D Huddle Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | OPEC1 | EKG Testing Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | OPHM1 | Holter Monitoring Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | OPPE1 | Echocardiograph Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | OPPE2 | Stress Echocardiograph Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | OPTM1 | Stress Testing Treadmill Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | OPTM2 | Tilt Table Testing Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | OPHM1 | Event / Holter Monitor Work Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | EXRC1 | Cardiology Exam Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | EXRC2 | Pacemaker ICD Interrogation Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | OFDC2 | Consult Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | XVC01 | ECHO Reading Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
CARDIOVASCULAR LABORATORY SERVICE Procedure Rooms | XVC01 | EKG Reading Station | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - General. The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Cardiovascular laboratory Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific cardiovascular laboratory service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Cardiovascular Laboratory AHU sheet and space requirements in the room data sheets (RDS) may be used.
Clinical Services Research & Development (CSR&D) | SB202 | CSR&D Female Staff Toilet, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Clinical Services Research & Development (CSR&D) | SB203 | CSR&D Male Staff Toilet, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Clinical Services Research & Development (CSR&D) | SB244 | CSR&D Housekeeping Aides Closet (HAC), Bldg Sprt | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV
Clinical Services Research & Development (CSR&D) | SB653 | CSR&D Mailroom, Lgstcs Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SB773 | CSR&D Conference / Mutlipurpose Storage Room, Lgstcs Svc | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - General. This is a small closet and does not require HVAC.
Clinical Services Research & Development (CSR&D) | SC715 | CSR&D Research Informatics Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Ventilation. Total ACH based on cooling load and HVAC equipment capacity, outside air per ASHRAE 62.1 -2016 or latest approved edition and provide as indicated in the air handling unit data sheet.
Clinical Services Research & Development (CSR&D) | SC727 | CSR&D Patient Interview Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SC728 | CSR&D Exam Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Note 1 | VAV |  | Note 1 - Temperature Control. If a single exam room is provided it shall have local temperature control. If more than one exam room see applicable sections of Chapter 2.
Clinical Services Research & Development (CSR&D) | SC729 | CSR&D Workroom, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SC812 | CSR&D Records Storage Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SS101 | CSR&D Conference / Mutlipurpose Room, Educ Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
Clinical Services Research & Development (CSR&D) | SS204 | CSR&D PI Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
Clinical Services Research & Development (CSR&D) | SS211 | CSR&D Touch-Down Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SS212 | CSR&D Collaboration Station, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SS216 | CSR&D Trainee Workstation, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SS218 | CSR&D Researcher Workstation, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SS221 | CSR&D Reception, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SS222 | CSR&D Waiting, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SS224 | CSR&D Private Call Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
Clinical Services Research & Development (CSR&D) | SS229 | CSR&D Coat Closet, Stff Sprt | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - General. This is a small closet and does not require HVAC.
Clinical Services Research & Development (CSR&D) | SS232 | CSR&D Female Staff Locker Room, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Clinical Services Research & Development (CSR&D) | SS241 | CSR&D Male Staff Locker Room, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Clinical Services Research & Development (CSR&D) | SS262 | CSR&D Staff Breakroom, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air. Return air is permitted if the lounge is not equipped with vending machines, microwave, refrigerator, etc., otherwise follow requirements in ASHRAE Standard 62.1 - 2016 or latest approved edition.
Clinical Services Research & Development (CSR&D) | SS268 | CSR&D Copy / Supply Alcove, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
Clinical Services Research & Development (CSR&D) | SS285 | CSR&D Huddle Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
Clinical Services Research & Development (CSR&D) | SV692 | CSR&D Vending Alcove, VC Svc | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
HOME | XXXX | Home Entry/Front Porch | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | No | VAV |  | Note 1 - General. Provide HVAC in the porch if enclosed.
HOME | CLHFY | Foyer | NA | NA | NA | NA | NA | NA | 4 | NA | Return | 35 | (o) | No | VAV |  | Note 1 - General. Since Foyer is part of a bedroom, individual room temperature control is not required.
HOME | CLHOF | Home Office | 75 | 24 | 70 | 21 | 60 | NA | 4 | 2 | Return | 35 | (o) | Yes | VAV
HOME | CLHLR | Living Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Unoccupied Mode. Provide a project-specific unoccupied control sequence to reduce or stop the HVAC during unoccupied hours.
HOME | CLHDR | Dining Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | ( - ) | Yes | VAV |  | Note 1 - Ventilation. Evaluate minimum outside air for ventilation based on ASHRAE 62.1-2016 or latest approved edition for food and beverage service establishments and if it exceeds 2 ACH use that value. | Note 2 - Unoccupied Mode. Provide a project-specific unoccupied control sequence to reduce or stop the HVAC during unoccupied hours.
HOME | IPK01 | Kitchen and Servery | 75 | 24 | 70 | 21 | 60 | NA | 6 | 2 | Exhaust G & S | 40 | (-) | Yes | CV |  | Note 1 - General. Space includes a pantry not requiring HVAC. | Note 2 - Outside Air Requirements. If this space is served by a dedicated air handling unit return air may be used. If the space is served by an air handling unit used for other occupied spaces then all air delivered to the kitchen shall be exhausted and no return shall be allowed. Adjust the minimum outside air for the air handling unit such that the entire system is at least 15% positive, while maintaining the kitchen negative to its surroundings. | Note 3: - Kitchen Exhaust For Kitchens With Dedicated Air Handling Units. An NFPA 96 dedicated exhaust system shall serve hoods over cooking equipment. When the kitchen hood systems are off the exhaust system shall exhaust at least 2 air changes per hour and shall maintain the kitchen negative relative to its surroundings. | Note 4: - Kitchen Exhaust For Kitchens Without Dedicated Air Handling Units. An NFPA 96 dedicated exhaust system shall serve hoods over cooking equipment. Supplemental exhaust shall ensure the kitchen space is maintained negative to its surrounding during all occupied times regardless of whether or not the kitchen hoods are operating.
HOME | SRS01 | Pantry | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - General. Space includes a pantry not requiring HVAC.
HOME | CLHKH | Kitchen Housekeeping Closet | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | ( - - ) | No | CV
HOME | JANC1 | Housekeeping Aides Closet | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | ( - - ) | No | CV
HOME | CLHDN | Den | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
HOME | CLHBD | Resident Bedroom | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (0) | Yes | VAV
HOME | CLHBR | Resident Bathroom | NA | NA | 70 | 21 | NA | NA | 10 | NA | Exhaust G | 40 | (-) | Yes | CV |  | Note 1 - Bathroom Ventilation. Bathroom total air change per hour (ACH) is achieved through exhaust only, with makeup air coming from the patient room supply system. | Note 2: - Bathroom Temperature Control. Bathrooms subject to heat loss shall be heated through a thermostatically controlled terminal unit.
HOME | CLHBS | Bathing Suite | 75 | 24 | 82 | 28 | 60 | NA | 10 | 2 | Exhaust S | 40 | (-) | Yes | CV |  | Note 1 - Bathing Suite Supply and Exhaust. Maintain minimum of 10 ACH or minimum required to maintain temperature. All exhaust shall be through a dedicated wet exhaust system designed with due consideration to removal of moisture laden air. Exhaust quantity shall maintain the bathing suite negative to its exterior.
HOME | TNPG1 | Toilet | NA | NA | 70 | 21 | NA | NA | 10 | NA | Exhaust S | 40 | (-) | Yes | CV |  | Note 1 - Bathroom Ventilation. Bathroom total air change per hour (ACH) is achieved through exhaust only, with makeup air coming from the bathing suite supply system. The bathroom shall be maintained negative to the bathing suite. Use the same wet exhaust system used to serve the bathing suite. | Note 2: - Bathroom Temperature Control. Bathrooms subject to heat loss shall be heated through a thermostatically controlled terminal unit.
HOME | CLHD | Laundry | 78 | 26 | 70 | 21 | 60 | NA | 10 | 2 | Exhaust G | 45 | (-) | Yes | CV |  | Note 1 - Dryer Vent. Coordinate dryer vent exhaust with actual equipment used. | Note 2: - General Exhaust and Room Air Balance. Provide constant volume supply and constant volume general exhaust to maintain minimum 10 ACH and negative space conditions when the dryers are off.
HOME | SPSU1 | Soiled Utility Room | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust G | 40 | (--) | No | CV |  | Note 1: - General Exhaust and Room Air Balance. Provide constant volume exhaust only to maintain a minimum of 10 ACH. Depending on the size of the room it may be necessary to provide a transfer air duct to keep the pressure on the door from being excessive (in excess of 0.08 inches WC. [20 Pascal]).
HOME | CLHS1 | Clean Linen Storage | NA | NA | NA | NA | NA | NA | 4 | NA | Return | 40 | ( + ) | Notes | CV |  | Note 1 - Storage Type. Two different configurations of the clean linen closet are described. | Note 2 - Small Closet. For small, unoccupied closet (60 sf to 80 sf [6 m2 to 7 m2] size) supply conditioned air under positive air pressure but do not provide room temperature control and ducted return air. Allow air to ex-filtrate to the adjoining space to maintain positive air balance. | Note 3 - Large Storage Closet. For large occupied storage closet (greater than 80 sf [7 m2]) provide a dedicated air terminal unit with room temperature control and ducted return air. Balance supply and return air flows to maintain positive air balance.
HOME | TNPG1 | Toilet - Resident / Visitor | NA | NA | 70 | 21 | NA | NA | 10 | NA | Exhaust (G) | 40 | ( - - ) | Yes | CV |  | Note 1 - Bathroom Ventilation. Bathroom total air change per hour (ACH) is achieved through exhaust only, with makeup air coming from the corridors. | Note 2: - Bathroom Temperature Control. Bathrooms subject to heat loss shall be heated through a thermostatically controlled terminal unit.
HOME | CLCHC | Hair Care (Barber/Beauty Salon) | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | ( - ) | Yes | VAV |  | Note 1 - Ventilation and Exhaust. Evaluate ventilation per ASHRAE Standard 62.1-2016 (or latest approved edition) and use that value if it exceeds 2 ACH.
HOME | CLHS2 | Home Storage | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - General. This is a small closet and does not require HVAC.
HOME | CLHGR | Garage | NA | NA | 50 | 10 | NA | NA | NA | NA | NA | 35 | (o) | Yes | CV |  | Note 1 - General. Provide a thermostatically-controlled heater for colder climates (40 F [5 C] and below) when the Garage is equipped with fire protection or water piping.
HOME |  | Corridor | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | ( + ) | Yes | VAV |  | Note - 1 General. The HVAC data is applicable to all corridors (circulation spaces) in the CLC/DOM. | Note - 2 Supply Air Volume. Adjust supply air volume as required to meet the transfer air demand of the adjoining spaces, such as, toilets, HACs and/or soiled utility rooms requiring negative air balance and exterior doors requiring ex-filtration.
COMMUNITY CENTER | LOB02 | Vestibule | NA | NA | 50 | 10 | NA | NA | NA | NA | NA | 40 | ( + ) | Yes | CV |  | Note 1 - Heating. Provide a thermostatically-controlled terminal heater. Coordinate heater type and location with the architectural discipline. Floor-mounted cabinet unit heaters with bottom horizontal supply and top return have proven effective in counter-acting cold air settling at the floor level. Heating for vestibules and for air curtains with integral heating shall include automatic controls capable of and configured to shut off the heating system when outdoor air temperatures are above 45°F. | Note 2 - Space Pressurization. Supply 1.0 cfm/sf [5.1 L/s/m2] air under positive pressure from an adjoining air terminal unit serving the lobby to maintain positive air pressure by allowing air to ex-filtrate outdoors. | Note 3 - Vestibule heating and cooling systems controls shall be capable of and configured to limit heating to a maximum of 60°F and cooling to a minimum of 85°F.
COMMUNITY CENTER | CLCCS | Concierge Station | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | ( - ) | Yes | VAV
COMMUNITY CENTER | CLCBB | Bistro | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | ( - ) | Yes | VAV |  | Note 1 - Ventilation. Evaluate minimum outside air for ventilation based on ASHRAE 62.1-2016 or latest approved edition for food and beverage service establishments and if it exceeds 2 ACH use that value.
COMMUNITY CENTER | CLCGR | Great Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | ( o ) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Provide a carbon-dioxide (CO2) and/or occupancy sensor to conserve energy during light occupancy. The control sequence shall be project-specific. Follow ASHRAE 62.1 - 2016 or latest approved edition requirements.
COMMUNITY CENTER | CLNMR | Multipurpose Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | ( o ) | Yes | VAV |  | Note 1 - Folding Partitions. Where the room is equipped with folding partitions, provide individual room temperature control for either side of the partition. Design the supply and return grill layout to operate at acceptable ADPI values with the partition open and with the partition closed. Include return grill on both sides of the partition. | Note 2 - Energy Conservation Initiative. Provide a carbon-dioxide (CO2) and/or occupancy sensor to conserve energy during light occupancy. The control sequence shall be project-specific. Follow ASHRAE 62.1 - 2016 or latest approved edition requirements.
COMMUNITY CENTER | STCL1 | Multipurpose Storage | NA | NA | 50 | 10 | NA | NA | NA | NA | NA | 40 | ( o ) | Yes | NA |  | Note 1 - Temperature Control. Storage rooms subject to heat loss shall be heated through a thermostatically controlled terminal unit.
COMMUNITY CENTER | CLCLB | Media Center | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | ( o ) | Yes | VAV |  | Note 1 - Equipment Heat Gain. Coordinate equipment heat gain with the equipment manufacturer.
COMMUNITY CENTER | CLCHC | Hair Care (Barber/Beauty Salon) | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | ( - ) | Yes | VAV |  | Note 1 - Minimum Ventilation. Evaluate minimum outside air for ventilation based on ASHRAE 62.1-2016 or latest approved edition for barber and beauty salon establishments and if it exceeds 2 ACH use that value. | Note 2 - Ducted Exhaust. Provide ducted exhaust per ASHRAE Standard 62.1-2016 or latest approved edition.
COMMUNITY CENTER | CFR01 | Conference Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | ( o ) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Provide a carbon-dioxide (CO2) and/or occupancy sensor to conserve energy during light occupancy. The control sequence shall be project-specific. Follow ASHRAE 62.1 - 2016 or latest approved edition requirements.
COMMUNITY CENTER | TNPG1 | Toilet - Resident / Visitor | NA | NA | 70 | 21 | NA | NA | 10 | NA | Exhaust (G) | 40 | ( - - ) | Yes | CV |  | Note 1 - Bathroom Ventilation. Bathroom total air change per hour (ACH) is achieved through exhaust only, with makeup air coming from the corridors. | Note 2: - Bathroom Temperature Control. Bathrooms subject to heat loss shall be heated through a thermostatically controlled terminal unit.
COMMUNITY CENTER | OFA09 | Administrative Office / Nursing Office / Activities Director's Office / Maintenance Office / Physician Office | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | ( o ) | Yes | VAV |  | Note 1 - Individual Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
COMMUNITY CENTER | SACP1 | Copy Room | 75 | 24 | 70 | 21 | 60 | NA | 6 | 2 | Return | 40 | ( o ) | Yes | VAV |  | Note 1 - Room Temperature Control. Copy Room may not require individual room temperature control if open to an adjoining space during the occupied mode. Room air from the adjoining space can be returned over the copy equipment to reduce heat concentration. | Note 2 - Exhaust Requirements. Provide general exhaust as required by ASHRAE Standard 62.1-2016 or latest approved edition.
COMMUNITY CENTER | SALG2 | Staff Lounge and Lockers | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 40 | ( - ) | Yes | CV
COMMUNITY CENTER | TNPG1 | Staff Toilet | NA | NA | 68 | 20 | NA | NA | 10 | NA | Exhaust (G) | 40 | ( - - ) | Yes | CV |  | Note 1 - Terminal Heater. Provide a thermostatically-controlled, terminal heater for the toilets subject to heat loss. | Note 2 - Transfer Air for Exhaust. For Staff Toilets located with the Staff Lounge and Lockers, provide transfer air for exhaust from the Staff Lounge and Lockers.
COMMUNITY CENTER | STCL1 / STC2 / CLCS3 | Storage: Multi-Purpose Room / General / Maintenance | NA | NA | 50 | 10 | NA | NA | NA | NA | NA | 40 | NA | Yes | NA |  | Note 1 - Terminal Heater. Provide a thermostatically-controlled, terminal heater for a storage room subject to heat loss and possibility of fire protection and/or water pipe freezing.
COMMUNITY CENTER | SPHC1 | HAC | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | ( - - ) | No | CV |  | Note 1 - Terminal Heater. Provide a thermostatically-controlled, terminal heater for a HAC room subject to heat loss and possibility of fire protection and/or water pipe freezing.
COMMUNITY CENTER | XXYYC | Satellite Telephone/Communications Closet | 68 | 20 | 68 | 20 | NA | NA | 6 | NA | Return | 40 | ( o ) | Yes | CV |  | Note 1 - General. The Satellite Telephone/Communication Closet (also known as Room) shall be served by a dedicated, cooling unit in operation on-demand and uninterrupted.
COMMUNITY CENTER | CLHGR | Garage | NA | NA | 60 | 15 | NA | NA | - | 100% | Exhaust (S) | 50 | ( - ) | Yes | CV |  | Note 1 - Ventilation (100% Outdoor Air) Provide a ventilation system complete with fan(s), exhaust and/or supply, and air inlet and outlet connections equipped with motorized dampers. Size and select the system to move air at the rate of 1.5 cfm/sf [7.6 L/s/m2]. | Note 2 - Heating. Provide thermostatically-controlled heat delivered either by the supply air system or individual air terminal units. During heating mode, reduce the outdoor air to minimum as mandated by ASHRAE Standard 62.1-2016 or latest approved edition and other applicable documents. | Note 3 - Compliance and Reference. The HVAC system shall be in compliance with the American Council of Government Industrial Hygienists (ACCIH) and NFPA 88B. Refer to the ASHRAE Handbook of Applications for further information.
COMMUNITY CENTER | CLCCH | Chapel/Meditation/Quiet Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Provide a carbon-dioxide (CO2) and/or occupancy sensor to conserve energy during light occupancy. The control sequence shall be project-specific. Follow ASHRAE 62.1 - 2016 or latest approved edition requirements.
COMMUNITY CENTER | XXXXX | Physicians Office | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - Individual Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
COMMUNITY CENTER | CLCEX3 | Exam Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - Individual Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
COMMUNITY CENTER | MEDP1 | Pharmacy | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | ( o ) | Yes | VAV
COMMUNITY CENTER | CLCOF | Security Office | 75 | 24 | 70 | 21 | 60 | NA | 4 | 2 | Return | 35 | ( o ) | Yes | VAV |  | Note 1 - Individual Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
COMMUNITY CENTER | CLCRC | Receiving and Loading | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (+) | Yes | VAV |  | Note 1: Air Curtain. Provide an air curtain with a heating element. Interlock the air curtain start sequence with the loading door dock operating mechanism. Activate heating when the ambient temperature falls below 45 F (7 C).
CENTRAL LAUNDRY FACILITY | [16 empty] | Note 1 - General: At the time this manual was published a VA central laundry design guide was not available in the VA TIL, therefore, the nomenclature of the spaces may not match future laundry design guides. To compensate for that the space names are descriptive by function. The actual room layouts, equipment disposition, and the HVAC parameters may vary with the project scope of work.
CENTRAL LAUNDRY FACILITY | XXXX | Soiled Receiving and Sorting Ante Room | NA | NA | NA | NA | NA | NA | 10 | 2 | None | 45 | (+) | No | CV |  | Note 1 – Soiled Receiving and Sorting Ante Room: If provided, this is an air lock space between the corridor outside the laundry and the soiled receiving space. The space shall have double doors to the corridor and double doors to the soiled receiving area. The leakage on these doors shall be analyzed to determine the amount of air required for pressurization. No return or exhaust shall be provided and temperature control shall be from the soiled receiving and sorting room.
CENTRAL LAUNDRY FACILITY | XXXX | Soiled Receiving and Sorting Room | 78 | 26 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G ) | 45 | (-) | Yes | CV |  | Note 1 – Soiled Receiving and Sorting Room This contaminated room is separated from the clean side by the washer / extractors and typically has a high ceiling mounted track system for trolley cars that are used to move the bags of laundry. Therefore the air supply ductwork and grills are mounted high above the tracks. The air distribution should be directional with supply slots or high wall grills blowing down at the far end away from the loading doors of the washer extractors towards the door and exhaust grills in a line directly above the washer / extractor doors.
CENTRAL LAUNDRY FACILITY | XXXX | Clean Laundry Work Room | 78 | 26 | 70 | 21 | 60 | 30 | 4 | 2 | Note 3 and 4 | 45 | (+) | Yes | CV |  | Note 1 – Clean Laundry Work Room. This uncontaminated space is separated from the soiled receiving and sorting room by the washer extractors and the washer extractor unload doors open into this space. The dryers, ironers, clean linen bins and other equipment are located in this space. | Note 2 – Air Distribution. This space also contains high ceiling mounted track system for trolley cars that are used to move the bags of laundry so that air distribution must be above and out of the way requiring high velocity side grills / drum louvers for proper air motion in the space. | Note 3 – Return and Local Exhaust. Provide local exhaust system above the unloading doors for the washer extractors to remove hot humid air when unloading the machines. Exhaust quantity shall not exceed minimum required ventilation (outdoor) air. Note the space is positive . | Note 4 – Special Exhaust. Provide direct ducted exhaust from dryers and ironers. See air handling unit data sheet for energy recovery opportunities.
CENTRAL LAUNDRY FACILITY | XXXX | Clean Laundry Storage Room | 78 | 26 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 45 | (+) | Yes | CV |  | Note 1 – Clean Laundry Storage Room. This uncontaminated space may be separate from the clean laundry work room or may be a designated storage area within the clean laundry work room. If it is not separate then temperature control shall be concurrent with the controls for the Clean Landry Work Room.
CENTRAL LAUNDRY FACILITY | OFA09 | Offices | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | 0 | Yes | VAV |  | Note 1 – Space Temperature Control. Provide VAV terminal and reheat.
CENTRAL LAUNDRY FACILITY | XXXX | Break Room / Staff Lounge | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust (G) | 40 | (-) | Yes | VAV |  | Note 1 - Room Air. Return air is permitted if the lounge space is not equipped with cooking equipment (microwave, hot plate, toasters).
DENTAL CLINIC Dental Suite | DNXS1 | X- Ray Panoramic / Cephalometric | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. Coordinate equipment heat gain with the manufacturer and evaluate resultant conditions. Remove heat by practical, available means. Adjust required temperature and humidity to match manufacturer's requirements.
DENTAL CLINIC Dental Suite | DNXC1 | Cone Beam Computerized Tomography | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. Coordinate equipment heat gain with the manufacturer and evaluate resultant conditions. Remove heat by practical, available means. Adjust required temperature and humidity to match manufacturer's requirements.
DENTAL CLINIC Dental Suite | DNXC2 | Cone Beam Computerized Tomography Control Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. Coordinate equipment heat gain with the manufacturer and evaluate resultant conditions. Remove heat by practical, available means. Adjust required temperature and humidity to match manufacturer's requirements.
DENTAL CLINIC Dental Suite | DNTG1 | Multi-functional Dental Treatment Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (+) | Yes | VAV
DENTAL CLINIC Dental Suite | DNTG5 | Special Needs Patient Dental Treatment Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (+) | Yes | VAV
DENTAL CLINIC Dental Suite | DNTS1 | Minor Procedure Room Oral Surgery | 75 | 24 | 70 | 21 | 60 | 30 | 15 | 3 | Return | 35 | (+) | Yes | CV |  | Note 1 - Space Classification. The design criteria are based on the assumption that the Oral Surgery Room is classified as Class A Surgery/Procedure Room (ASHRAE Standard 170 - 2016 or latest approved edition). The designer shall verify the requirements with the end-users and modify the classification, if necessary. | Note 2 - Nitrous Oxide Gas. Where nitrous oxide gas is used, the design shall implement the recommendation of National Institute for Occupational Safety and Health (NIOSH) to limit the occupational exposure within the prescribed limits by installing a local scavenging system. Compliance is also required to NFPA 99 for other safety requirements.
DENTAL CLINIC Dental Suite | DNSC3 | Sterile Instrument Storage | 66 | 19 | 72 | 22 | 55 | 30 | 4 | 4 | Return | 40 | (+) | Yes | CV
DENTAL CLINIC Dental Suite | MECH1 | Dental Equipment Mechanical Room | 80 | 27 | 65 | 18 | N/A | N/A | N/A | N/A | Exhaust (G) | 40 | (-) | No | VAV/CV |  | Note 1 - General. Coordinate equipment heat gain with the manufacturer and evaluate resultant conditions. Remove heat by practical, available means.
DENTAL CLINIC Dental Suite | DNPL1 | General Purpose Laboratory | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 40 | (-) | Yes | VAV |  | Note 1 - Exhaust from Prosthetic Dental Workstation. Provide exhaust from the prosthetic dental workstation either by wall registers, installed at the table height, or by a canopy hood. Exhaust can be connected to the general exhaust system. Estimate the exhaust air volume based on the geometry of the work area. | Note 2 - Heat Gain. Coordinate equipment heat gain with the manufacturer. | Note 3 - Boil-Out Sink and Casing Soldering Areas. Provide exhaust over the boil-out sink and case-soldering area using a canopy hood, connected to a general exhaust system, and sized at 100 fpm [0.5 m/s] face velocity. Coordinate the hood size and location with the architectural drawings.
DENTAL CLINIC Dental Suite | DNPC1 | Laboratory Porcelain / Ceramics | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 40 | (-) | Yes | VAV |  | Note 1: Heat Gain. Coordinate equipment heat gain with the manufacturer. | Note 2 - Exhaust Air Intakes. Locate exhaust registers and / or exhaust hoods at or near the technician's workbench. Coordinate with architectural and electrical drawings.
DENTAL CLINIC Dental Suite | DNTR1 | Patient Prep / Recovery Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+) | Yes | VAV
DIALYSIS CENTER | XXYYC | Renal Dialysis Private Bed Station | 78 | 26 | 72 | 22 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
DIALYSIS CENTER | RDC02 | Renal Dialysis Negative Isolation Private Bed Station | 78 | 26 | 72 | 22 | 60 | 30 | 12 | 2 | Exhaust (S) | 35 | (--) | Yes | CV |  | Note 1 - Negative Isolation Pressure Bed Station. See additional requirements on Room Data Sheets for Infectious Isolation rooms.
DIALYSIS CENTER | RDC01 | Renal Dialysis Cubicle Chair Station | 78 | 26 | 72 | 22 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
DIALYSIS CENTER | XXYYC | Renal Dialysis Cubicle Bed Station | 78 | 26 | 72 | 22 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
DIALYSIS CENTER | CSDE1 | Equipment Processing Soiled Receiving | 78 | 26 | 72 | 22 | 60 | 30 | 10 | NR | Exhaust (G) | 40 | (--) | Yes | CV
DIALYSIS CENTER | CSSS1 | Equipment Processing Clean Preparation | 78 | 26 | 72 | 22 | 60 | 30 | 10 | NR | Exhaust (G) | 40 | (-) | Yes | CV
DIALYSIS CENTER | CSIA1 | Equipment Processing Clean Storage | 70 | 21 | 70 | 21 | 55 | 30 | 4 | 4 | Return | 40 | (+) | Yes | CV
DIGESTIVE DISEASES - ENDOSCOPY SERVICE Procedure Room | TREE1 | Endoscopy Procedure | 68 | 20 | 73 | 23 | 60 | 30 | 10 | 2 | Exhaust (G) | 35 | (o) | Yes | CV |  | Note 1 - General: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Digestive Diseases - Endoscopy Service Design Guide dated November 29, 2011. Endoscopy services suites constructed prior to this may also contain procedure rooms lists as proctoscopy, sigmoidoscopy, and colonoscopy, EGD. In the current practice all these procedures take place in the same space. | Note 2 - Air Handling Unit: If the size and / or arrangement of a specific endoscopy service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements in the Digestive Diseases AHU sheet and the space requirements on this sheet may be used. Provide in the design constant volume pressure independent reheat terminals to maintain the required constant volume air flows regardless of AHU type and operation. | Note 3 - Endoscopy Procedure: Includes, but not limited to all endoscopy, anoscopy, proctoscopy, colonoscopy, sigmoidoscopyEGD, ERCP etc.(a) Neutral room airflow pattern is acceptable if only GI procedures are performed. If there is reasonable likelihood the procedure room will be used for more than one type of procedure (e.g., GI endoscopy and bronchoscopy), the room must meet the most stringent criteria for the types of procedures to be performed in the room. (b) Existing GI Endoscopy Procedure Rooms can meet original design standards required at the time of build if GI procedures only are performed in the room. If other procedures are performed besides GI procedures (e.g., bronchoscopy), the room must meet the standards/most stringent criteria for the types of procedures performed. | Note 4 - Room Air Balance. (a) If the above procedures are performed on a patient suspected of tuberculosis or similar infectious disease, the procedure room must be maintained under negative air balance and the room air should be exhausted outdoors without mixing with any other general exhaust.
DIGESTIVE DISEASES - ENDOSCOPY SERVICE Procedure Room | TREE2 | Endoscopic Ultrasound Procedure (ERCP) | 68 | 20 | 73 | 23 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV |  | Note 1 - General: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Digestive Diseases - Endoscopy Service Design Guide dated November 29, 2011. Endoscopy services suites constructed prior to this may also contain procedure rooms lists as proctoscopy, sigmoidoscopy, and colonoscopy, EGD. In the current practice all these procedures take place in the same space. | Note 2 - Air Handling Unit: If the size and / or arrangement of a specific endoscopy service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements in the Digestive Diseases AHU sheet and the space requirements on this sheet may be used. Provide in the design constant volume pressure independent reheat terminals to maintain the required constant volume air flows regardless of AHU type and operation. | Note 3 - Room Air Balance. (a) If the above procedures are performed on a patient suspected of tuberculosis or similar infectious disease, the procedure room must be maintained under negative air balance and the room air should be exhausted outdoors without mixing with any other general exhaust.
DIGESTIVE DISEASES - ENDOSCOPY SERVICE Procedure Room | USCL2 | Scope Decontamination Room | 66 | 19 | 72 | 22 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (--) | Yes | CV |  | Note 1 - General: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Digestive Diseases - Endoscopy Service Design Guide dated November 29, 2011. Endoscopy services suites constructed prior to this may also contain procedure rooms lists as proctoscopy, sigmoidoscopy, and colonoscopy, EGD. In the current practice all these procedures take place in the same space. | Note 2 - Air Handling Unit: If the size and / or arrangement of a specific endoscopy service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements in the Digestive Diseases AHU sheet and the space requirements on this sheet may be used. Provide in the design constant volume pressure independent reheat terminals to maintain the required constant volume air flows regardless of AHU type and operation. | Note 3 - Scope Decontamination Room: See SPS for additional requirements of scope decontamination and processing rooms.
DIGESTIVE DISEASES - ENDOSCOPY SERVICE Procedure Room | USCL3 | Scope Reprocess | 66 | 19 | 72 | 22 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - General: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Digestive Diseases - Endoscopy Service Design Guide dated November 29, 2011. Endoscopy services suites constructed prior to this may also contain procedure rooms lists as proctoscopy, sigmoidoscopy, and colonoscopy, EGD. In the current practice all these procedures take place in the same space. | Note 2 - Air Handling Unit: If the size and / or arrangement of a specific endoscopy service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements in the Digestive Diseases AHU sheet and the space requirements on this sheet may be used. Provide in the design constant volume pressure independent reheat terminals to maintain the required constant volume air flows regardless of AHU type and operation.
DIGESTIVE DISEASES - ENDOSCOPY SERVICE Procedure Room | USCL4 | Clean Scope Storage | 66 | 19 | 72 | 22 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | CV |  | Note 1 - General: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Digestive Diseases - Endoscopy Service Design Guide dated November 29, 2011. Endoscopy services suites constructed prior to this may also contain procedure rooms lists as proctoscopy, sigmoidoscopy, and colonoscopy, EGD. In the current practice all these procedures take place in the same space. | Note 2 - Air Handling Unit: If the size and / or arrangement of a specific endoscopy service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements in the Digestive Diseases AHU sheet and the space requirements on this sheet may be used. Provide in the design constant volume pressure independent reheat terminals to maintain the required constant volume air flows regardless of AHU type and operation.
DIGESTIVE DISEASES - ENDOSCOPY SERVICE Procedure Room | RRSS1 | Prep and Recovery | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV |  | Note 1 - General: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Digestive Diseases - Endoscopy Service Design Guide dated November 29, 2011. Endoscopy services suites constructed prior to this may also contain procedure rooms lists as proctoscopy, sigmoidoscopy, and colonoscopy, EGD. In the current practice all these procedures take place in the same space. | Note 2 - Air Handling Unit: If the size and / or arrangement of a specific endoscopy service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements in the Digestive Diseases AHU sheet and the space requirements on this sheet may be used. Provide in the design constant volume pressure independent reheat terminals to maintain the required constant volume air flows regardless of AHU type and operation. | Note 3 - Room Air Balance. (a) If the above procedures are performed on a patient suspected of tuberculosis or similar infectious disease, the procedure room must be maintained under negative air balance and the room air should be exhausted outdoors without mixing with any other general exhaust.
DOMICILIARY | OFDC2 | Consult Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Note 1 | VAV |  | Note 1 - Temperature Controls. If one room is provided provide it with temperature control. If more than one room is provided follow Chapter 2 requirements.
DOMICILIARY | DAYR1 | Patient Lounge | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Folding Partitions. Where the room is equipped with folding partitions, provide individual room temperature control for either side of the partition. Design the supply and return grill layout to operate at acceptable ADPI values with the partition open and with the partition closed. Provide return grill on both sides of the partition. | Note 2 - Energy Conservation Initiative. Provide a carbon-dioxide (CO2) and/or occupancy sensor to conserve energy during light occupancy. The control sequence shall be project-specific. Comply with the requirements of ASHRAE 62.1 - 2016 or latest approved edition.
DOMICILIARY | BRUN1 | One-Bed Bedroom Addiction Treatment Program / Homeless Program / Health Maintenance Program / PTSD Program / Brain Injury Program | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
DOMICILIARY | BRUN1 | Two-Bed Bedroom Addiction Treatment Program / Homeless Program / Health Maintenance Program / PTSD Program | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
DOMICILIARY | TSPB1 | Toilet / Shower, Bariatric | NA | NA | 70 | 21 | NA | NA | 10 | NA | Exhaust G | 40 | (-) | Yes | CV |  | Note 1 - Bathroom Ventilation. Bathroom total air change per hour (ACH) is achieved through exhaust only, with makeup air coming from the patient room supply system. | Note 2 - Bathroom Temperature Control. Bathrooms subject to heat loss shall be heated through a thermostatically controlled terminal unit.
DOMICILIARY | XXYYC | Multiple Living Unit Sleeping Area | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
DOMICILIARY | TSPG1 | Multiple Living Unit, Toilet / Shower | NA | NA | 70 | 21 | NA | NA | 10 | NA | Exhaust G | 40 | (-) | Yes | CV |  | Note 1 - Bathroom Ventilation. Bathroom total air change per hour (ACH) is achieved through exhaust only, with makeup air coming from the patient room supply system.
ELECTRONENCEPHALOGRAPHY LABORATORY (EEG) Procedure Room | OPEE1 | EEG Exam Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | No | VAV |  | Note 1 - General The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Electroencephalography Laboratory (EEG) Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific EEG service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements in the EEG Laboratory AHU sheet and the space requirements on this sheet may be used.
ELECTRONENCEPHALOGRAPHY LABORATORY (EEG) Procedure Room | EXRE2 | EMG Exam Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | No | VAV |  | Note 1 - General The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Electroencephalography Laboratory (EEG) Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific EEG service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements in the EEG Laboratory AHU sheet and the space requirements on this sheet may be used.
ELECTRONENCEPHALOGRAPHY LABORATORY (EEG) Procedure Room | OPPF8 | Patient Prep Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | No | VAV |  | Note 1 - General The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Electroencephalography Laboratory (EEG) Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific EEG service warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements in the EEG Laboratory AHU sheet and the space requirements on this sheet may be used.
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | BRAR1 | Negative Pressure Isolation Anteroom | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (S) | 35 | Note 1 | No | CV |  | Note 1 - General: See Infectious Isolation Room Data Sheets for more information. Note that dual purpose negative / positive isolation rooms are prohibited.
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | TRET4 | Exam / Treatment Room, Negative Pressure Isolation | 75 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Exhaust (S) | 35 | Note 1 | Yes | CV |  | Note 1 - General: See Infectious Isolation Room Data Sheets for more information. Note that dual purpose negative / positive isolation rooms are prohibited.
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | TRET4 | Exam / Treatment Room, Positive Pressure Isolation | 75 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Return | 35 | Note 1 | Yes | CV |  | Note 1 - General: See Infectious Isolation Room Data Sheets for more information. Note that dual purpose negative / positive isolation rooms are prohibited.
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | UCCL1 | Clean Utility Room | 70 | 21 | 70 | 21 | 55 | 30 | 4 | 2 | Return | 40 | ( + ) | Yes | CV
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | OPMH4 | Examination Room Security | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | TLTP1 | Examination Room Security Toilet | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | ( - ) | No | CV
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | TRET3 | Resuscitation Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | NSTA1 | Team Workroom | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | No | VAV
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | TRET4 | Exam / Treatment Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | TRET6 | Bariatric Exam / Treatment Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | EXTR1 | Triage Room | 75 | 24 | 70 | 21 | 50 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | EXRG4 | Vital Sign Station | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV
EMERGENCY DEPARTMENT - The information indicated for this room is out-of-date. Please refer to Room Data Sheets in the Section 6 of the HVAC Design Manual for the most recent information. | WTG04 | General Waiting Room | 75 | 29 | 70 | 21 | 60 | 30 | 12 | 2 | Exhaust (G) | 35 | ( - ) | Yes | CV |  | Note 1 - Infection Control. Emergency waiting room shall be 100% exhausted and maintained negative to adjacent spaces.
EYE CLINIC | EYOT2 | Exam / Treatment Room, Optometry | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Temperature Control. If more than one space is provided follow Chapter 2 requirements for temperature control zones.
EYE CLINIC | TREY2 | Laser Room | 75 | 24 | 70 | 21 | 60 | 30 | 15 | 3 | Return | 35 | (+) | Yes | CV
Health Services Research & Development (HSR&D) | SB202 | HSR&D Female Staff Toilet, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Health Services Research & Development (HSR&D) | SB203 | HSR&D Male Staff Toilet, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Health Services Research & Development (HSR&D) | SB244 | HSR&D Housekeeping Aides Closet (HAC), Bldg Sprt | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV
Health Services Research & Development (HSR&D) | SB653 | HSR&D Mailroom, Lgstcs Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Health Services Research & Development (HSR&D) | SB773 | HSR&D Conference / Multipurpose Storage Room, Lgstcs Svc | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - General. This is a small closet and does not require HVAC.
Health Services Research & Development (HSR&D) | SC715 | HSR&D Research Informatics Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Health Services Research & Development (HSR&D) | SC813 | HSR&D Records Storage Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Health Services Research & Development (HSR&D) | SS101 | HSR&D Conference / Multipurpose Room, Educ Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
Health Services Research & Development (HSR&D) | SS204 | HSR&D PI Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
Health Services Research & Development (HSR&D) | SS211 | HSR&D Touch-Down Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Health Services Research & Development (HSR&D) | SS212 | HSR&D Collaboration Station, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
Health Services Research & Development (HSR&D) | SS216 | HSR&D Trainee Workstation, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Health Services Research & Development (HSR&D) | SS218 | HSR&D Researcher Workstation, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Health Services Research & Development (HSR&D) | SS221 | HSR&D Reception, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Health Services Research & Development (HSR&D) | SS222 | HSR&D Reception, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Health Services Research & Development (HSR&D) | SS224 | HSR&D Private Call Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
Health Services Research & Development (HSR&D) | SS229 | HSR&D Coat Closet, Stff Sprt | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - General. This is a small closet and does not require HVAC.
Health Services Research & Development (HSR&D) | SS232 | HSR&D Female Staff Locker Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Health Services Research & Development (HSR&D) | SS241 | HSR&D Male Staff Locker Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Health Services Research & Development (HSR&D) | SS262 | HSR&D Staff Breakroom, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air. Return air is permitted if the lounge is not equipped with vending machines, microwave, refrigerator, etc., otherwise follow requirements in ASHRAE Standard 62.1 - 2016 or latest approved edition.
Health Services Research & Development (HSR&D) | SS268 | HSR&D Copy / Supply Alcove, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
Health Services Research & Development (HSR&D) | SS285 | HSR&D Huddle Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
Health Services Research & Development (HSR&D) | SV692 | HSR&D Vending Alcove, VC Svc | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
IMAGING SERIES (MRI UNIT) | XMRC1 | MRI Control Room | 75 | 24 | 70 | 21 | 50 | 30 | 6 | 2 | Return Exhaust (G) | 40 | (o) | Yes | VAV |  | Note 1- Construction Coordination. Carefully coordinate all technical requirements indicated herein with the specific MRI system being installed. Also, carefully coordinate contractual requirements of the MRI systems installation with the MRI manufacturer's requirements. For example in many cases the MRI manufacturer's warranty requires chilled water system startup to be by the manufacturer and in that event the HVAC design documents have to provide a specific piping and instrument manifold that allows chilled water system startup prior to MRI installation. Review all requirements and coordinate.
IMAGING SERIES (MRI UNIT) | XMRS1 | MRI Scanning Room | 68 | 20 | 70 | 21 | 50 | 40 | 12 | 2 | Return Exhaust (S) | 35 | (o) | Yes | VAV |  | Note 1- Construction Coordination. Carefully coordinate all technical requirements indicated herein with the specific MRI system being installed. Also, carefully coordinate contractual requirements of the MRI systems installation with the MRI manufacturer's requirements. For example in many cases the MRI manufacturer's warranty requires chilled water system startup to be by the manufacturer and in that event the HVAC design documents have to provide a specific piping and instrument manifold that allows chilled water system startup prior to MRI installation. Review all requirements and coordinate. | Note 2- MRI Scanning Room Temperature. MRI scanners' image quality can be degraded by environmental conditions outside of the equipment manufacturer's specifications. MRI Scanning Room temperature shall be maintained between 68 F - 70 F [20 C - 21 C] under both heating and cooling conditions. | Note 3 - Emergency Exhaust Fan. (a) Provide a special automatic/manual emergency exhaust system to exhaust the scanning room in the event cryogen spills in the room. (b) Automatic operation of the exhaust system shall be interlocked to the MRI equipment vendor automatic alarm system (if provided) by an electric relay. Provide two manual switches (one located in the scanning room and the other in the control room) under the custody of the designated operating personnel. (c) Exhaust fan can discharge from the walls or roof if there are no operable windows or outside air intakes, or if regular or scheduled human traffic is not within a 25 ft [7.6 m] radius. Provide a motorized damper in the return air duct to stop return air pick up. (d) Provide a laser optical oxygen sensor, located 18 in [450 mm] below the suspended architectural ceiling, to sound an audible and visible local alarm and an alarm at the ECC in the event the oxygen level drops. Alternatively, if saturable sensor oxygen monitor systems are used, these shall be located outside the MRI Scanning Room with a sampling tube entering the MRI Scanning Room at 18 in [450 mm] below the suspended architectural ceiling. Coordinate any and all penetrations of the required RF shield assembly with the RF shield vendor. Alarm shall automatically activate the emergency exhaust fan operation sequence. | Note 4 - Cryogen (Quench) Vent Pipe. (a) Provide a vent pipe (size, location, and material to be coordinated with the MRI equipment supplier) from the RF shield to outdoors. (b) Divide the scope of work such that the MRI vendor is responsible for the supply and installation of the vent pipe, including RF Shield fitting, from the magnet to the RF Shield Barrier. (c) Helium gas vent can discharge horizontally, through exterior walls, or vertically, though the roof. For both discharge conditions, there shall be no operable windows or outside air intakes, and no regular or scheduled human traffic within 25 ft [7.6 m] radius in all directions. Terminate the vent pipe with a turndown weather head. Horizontal chamfered terminations are not permitted. Termination shall be protected from horizontal wind driven rain entry. Insulate the quench piping from the MRI connection to termination. Insulation shall be calcium silicate type. (d) Provide manual quench activation switches if required by the MRI manufacturer. Coordinate with specific system used. | Note 5 - Overpressure Relief. (a) Hatch in RF Shield Enclosure: MRI equipment vendor shall be responsible for the supply, installation, and testing of the pressure relief hatch (gravity-operated). The hatch shall be similar to a back draft damper. Upon sensing a difference in pressure between the occupied space and the void between the suspended ceiling and the RF Shield enclosure, the hatch shall open to permit the cryogen gas to escape into the void between the RF Shield and the floor or roof above. (b) Hatch in the Roof or Wall: Install an "explosion" hatch in the roof or wall, whichever is the closest, to relieve gas under pressure to the outdoors. The explosion hatch is pressure-actuated and can be connected to the quench alarm system. Coordinate the location, size and design or the hatch with the MRI equipment vendor. Provide snow/ice melt systems in hatch cover as indicated by position and local climate. | Note 6 - Optional MRI Equipment Circulating Fan (Room Air Distribution). (a) At the MRI vendor's option, room air can be circulated through the MRI equipment by a dedicated circulating fan and returned back to the system by an indirect (thimble) connection. Coordinate the division in the scope of work between the MRI vendor and the general contractor. (b) Arrange room air distribution to allow the conditioned air to flow over/through the MRI scanner with return and/or exhaust inlets located at the rear of the equipment back to facilitate MRI equipment cooling. | Note 7 - Ductwork and Devices.(a) All active devices (VAVs, fan coil units, dampers, humidifiers, sensors or detectors) shall be located outside the MRI Scanning Room. (b) Ductwork, hangers, fasteners and appurtenances used within the MRI Scanning room plenum should be of non-magnetic materials and construction (e.g. aluminum). (c) MRI manufacturer may recommend supply and return duct penetrations both enter the MRI Scanning Room from the MRI System Component room. Coordinate locations/routes. (d) All piping and ductwork penetrations of MRI Scanning Room RF shield must be carefully coordinated with MRI manufacturer's and RF shield vendors' sitting requirements.
IMAGING SERIES (MRI UNIT) | XMRC2 | MRI Systems Component Room | 70 | 21 | 70 | 21 | 60 | 40 | 6 | 2 | Return | 40 | (o) | Yes | CV |  | Note 1 - HVAC System. (a) Provided a dedicated air conditioning unit to serve the System Component Room. Coordinate size and configuration with the equipment manufacturer. Coordinate air distribution with the raised floor. Provide water sensor alarm (local and at the ECC) in the event of water leakage below the raised floor. (b) Provide a closed loop, dedicated, water chiller to cool the MRI equipment. Chiller shall be air cooled and remotely located. Provide cross connections with the central chilled water plant. Additional considerations are: Ensure that the water quality (pH value, hardness, and solid suspended contents) are in accordance with the equipment manufacturer's specifications. All piping from the System Component Room entering the MRI Scanning Room shall meet "Radio Frequency Requirements." Provide clearly marked and identified access for the piping located in walls and chases. Coordinate chilled water flow requirement, chilled water temperature, and division in scope of work (connection detail) at each chilled water connection.
IMAGING SERIES (MRI UNIT) | WTG04 | MRI Visiting Area | 75 | 24 | 70 | 21 | 50 | 40 | 6 | 2 | Return | 40 | (o) | Yes | VAV
IMAGING SERIES (NUCLEAR MEDICINE SERVICES) | XDBD1 | Bone Densitometry Room | 70 | 21 | 70 | 21 | 50 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (NUCLEAR MEDICINE SERVICES) | NMGS1 | Nuclear Medicine Scanning Room (Patient Examination Room) | 75 | 24 | 70 | 21 | 50 | 30 | 6 | 2 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Air Balance. Provide visual indicator to demonstrate negative air balance. Exhaust space at 115% of supply air flow. | Note 2 - Air Distribution. Locate supply and exhaust air outlets to create a directional airflow and transfer air from the adjoining area. Locate 50% of exhaust air outlets at ceiling level and 50% of exhaust air outlets at 7 in [175 mm] above finished floor. | Note 3 - Xenon Gas. If xenon gas is used in this room, coordinate with the local radiation safety officer for any additional measures.
IMAGING SERIES (NUCLEAR MEDICINE SERVICES) | NMRP1 | Nuclear Medicine “Hot Lab” / Radiopharmacy | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Fume Hoods. This room is also known as the Radiopharmacy Room. Coordinate quantity and type of fume hoods and/or biological safety cabinets and provide an appropriate, dedicated exhaust system(s) to serve the hoods. See Chapter 3. If radioactive xenon gas and/or radioactive iodine are used in this space, coordinate with the local radiation safety officer for additional measures necessary, if any. Provide a supplementary general exhaust system, if required per the room air balance. | Note 2 - Air Balance. Provide volumetric controls to demonstrate negative air balance. | Note 3 - Air Distribution. Locate supply and exhaust air outlets to create a directional airflow and transfer air from the adjoining area.
IMAGING SERIES (NUCLEAR MEDICINE SERVICES) | NMIR1 | Patient Dose Administration | 75 | 24 | 70 | 21 | 50 | 30 | 6 | 2 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Air Balance. Provide visual indicator to demonstrate negative air balance. Exhaust space at 115% of supply air flow. | Note 2 - Air Distribution. Locate supply and exhaust air outlets to create a directional airflow and transfer air from the adjoining area.
IMAGING SERIES (NUCLEAR MEDICINE SERVICES) | NMRCR1 | PET/CT Control Room | 70 | 21 | 70 | 21 | 55 | 40 | 6 | 2 | Exhaust (G) | 35 | (+) | Yes | VAV
IMAGING SERIES (NUCLEAR MEDICINE SERVICES) | NMSS1 | PET/CT Scanning Room | 70 | 21 | 70 | 21 | 55 | 40 | 12 | 2 | Exhaust (G) | 35 | (-) | Yes | VAV |  | Note 1 - Air Balance. Provide volumetric controls to demonstrate negative air balance. | Note 2 - Air Distribution. Locate supply and exhaust air outlets to create a directional airflow and transfer air from the adjoining area. Locate 50% of exhaust air outlets at ceiling level and 50% of exhaust air outlets at 7 in [175 mm] above finished floor.
IMAGING SERIES (NUCLEAR MEDICINE SERVICES) | XMRC2 | PET/CT System Component Room | 70 | 21 | 70 | 21 | 50 | 40 | 6 | 2 | Exhaust (G) | 40 | (+) | Yes | VAV |  | Note 1 - HVAC System. (a) Provided a dedicated air conditioning unit to serve the System Component Room. Coordinate size and configuration with the equipment manufacturer. Coordinate air distribution with the raised floor. Provide water sensor alarm (local and at the ECC) in the event of water leakage below the raised floor. (b) Provide a closed loop, dedicated, water chiller to cool the PET/CT equipment. Chiller shall be air cooled and remotely located. Provide cross connections with the central chilled water plant. Additional considerations are: Ensure that the water quality (pH value, hardness, and solid suspended contents) are in accordance with the equipment manufacturer's specifications. Provide clearly marked and identified access for the piping located in walls and chases. Coordinate chilled water flow requirement, chilled water temperature, and division in scope of work (connection detail) at each chilled water connection. (c) Coordinate technical and contractual requirements with manufacturer of PET/CT system. Ensure chilled water equipment, if provided by PET/CT manufacturer is installed by mechanical contractor and powered by electrical contractor. Ensure system startup is consistent with PET/CT manufacturer's requirements and provide pipe manifolds and instruments needed for startup.
IMAGING SERIES (NUCLEAR MEDICINE SERVICES) | NMRP1 | Radio Chemistry Room | 75 | 24 | 70 | 21 | 60 | 30 | 10 | 2 | Exhaust (G) | 40 | (-) | Yes | VAV |  | Note 1 - Air Balance. Provide volumetric controls to demonstrate negative air balance.
IMAGING SERIES (RADIATION THERAPY SERVICES) | XTSC1 | CT Simulator Control Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XTSG1 | CT Simulator Unit Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XTLA1 | Linear Accelerator (IMRT) Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XTLC1 | Linear Accelerator Control Area | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XTTP1 | Treatment Planning Computer Room - Dosimetry Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XDUS1 | Ultrasound Planning Unit Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | (o) | Yes | CV |  | Note 1 - Air Balance. Maintain negative room air balance in adjoining toilet by 100% exhaust of toilet at 10 ACH.
IMAGING SERIES (RADIATION THERAPY SERVICES) | XCTC1 | CT Area - Control Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XCTS1 | CT Area - Scanning Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XACR1 | IR Area - Control Room | 75 | 24 | 70 | 21 | 60 | 30 | 15 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XABP1 | IR Area - Procedure Room | 66 | 24 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 35 | (+) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XACV1 | IR Area - System Component Room | 70 | 21 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XDCS1 | Patient Area - Chest Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XDR01 | Patient Area - Head Room/ Tomography | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XDR01 | Patient Area - General Purpose Radiology Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV |  | Note - Communicable Disease Isolation. See Communicable Disease Isolation room requirements elsewhere in Chapter 6 tables if a room needs to be provided with isolation capability.
IMAGING SERIES (RADIATION THERAPY SERVICES) | XDM01 | Mammography Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV
IMAGING SERIES (RADIATION THERAPY SERVICES) | XDRF1 | Patient Area - Radiographic/Fluoroscopic Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | CV |  | Note 1 - Alternate Exhaust System. Provide a special exhaust system and maintain the room under negative air balance if the procedures involve the use of noxious gases and / or chemical vapors, generally contained in a hood. Coordinate hood size and type with the equipment drawings.
IMAGING SERIES (RADIATION THERAPY SERVICES) | XDUS1 | Patient Area - Ultrasound Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | (o) | Yes | CV |  | Note 1 - Air Balance. Maintain negative room air balance in adjoining toilet by 100% exhaust of 10 ACH.
IMAGING SERIES (RADIATION THERAPY SERVICES) | WTG03 | Radiology Waiting Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | CV |  | Note 1 - Risk Assessment. Conduct risk assessment to determine if radiology waiting room should be 100% exhausted and maintained negative. If warranted design the HVAC for this room as indicated in Table 7.1 of the ASHRAE Standard 170 - 2016 or latest approved edition.
INFECTIOUS ISOLATION AND PROTECTIVE ENVIRONMENT |  | Infectious Isolation Rooms and Protective Environments | [14 empty] | Note 1 - General. Isolation Rooms are classified into two categories: Airborne Infection Isolation (AII), and Protective Environment (PE). Combining the two types of rooms is strictly prohibited. An ante room shall be provided for every PE room and for every AII room. Room codes assigned to these rooms will vary based on the clinical function in which they are being used. (a) Ante Rooms facilitate intended design air balance and maintain pressure differentials. (b) Ante Rooms provide better protection by isolating PE patients from the adjoining environment and the adjoining environment from the AII patient. (c) Ante Rooms provide the space required to don protective equipment before entering the isolation room. (d) Ante Rooms can be used for hand hygiene and storage of personal protective equipment and clean equipment. (e) ACH ventilation rates are minimum, actual number shall be the higher of 12 ACH, CFM required for cooling load, and CFM required to maintain required space pressure differential between the AII room and the anteroom. The differential shall be calculated based on the installed door size and characteristics. Coordinate with architecture.
INFECTIOUS ISOLATION AND PROTECTIVE ENVIRONMENT | XXXXX | Infectious Isolation Rooms Aii Ante Room | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (S) | 35 | (-) | No | CV |  | Note 1 - Special Exhaust System. Provide a dedicated, special exhaust system for the Patient Bedroom, Ante Room and Patient Toilet (where present). Do not connect rooms other than infection isolation rooms to the dedicated exhaust system. Locate the exhaust fan at the end of the duct run to maintain the ductwork within the building at a negative pressure and install bag-in-bag out HEPA filters just prior to the fan inlet. Discharge exhaust air above the highest roof level through a stack at least 10 ft [3 m] tall at 3,500 fpm [18 m/s] discharge velocity. The discharge air outlet shall be located at least 25 ft [8 m] from outdoor air intakes and operable windows. Follow the recommendations of the dispersion analysis for higher than minimum requirements. Provide emergency power for the exhaust fan and associated controls. Label ductwork, filter, and fan "COMMUNICABLE DISEASE CONTAMINATED AIR". Where ever practical connect as many AII rooms as possible to one exhaust system. In all cases provide two exhaust system and operate in LEAD/LAG configuration with automatic controls to turn on LAG fan upon LEAD fan failure. | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. AII Ante Room. Air shall transfer from the Corridor into the Ante Room and then to the Isolation Room. The Ante Room is positive with respect to the Isolation Room and negative with respect to the Corridor.
INFECTIOUS ISOLATION AND PROTECTIVE ENVIRONMENT | XXXXX | Infectious Isolation Rooms Aii Isolation Room | 75 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Exhaust (S) | 35 | (--) | Yes | CV |  | Note 1 - Special Exhaust System. Provide a dedicated, special exhaust system for the Patient Bedroom, Ante Room and Patient Toilet (where present). Do not connect rooms other than infection isolation rooms to the dedicated exhaust system. Locate the exhaust fan at the end of the duct run to maintain the ductwork within the building at a negative pressure and install bag-in-bag out HEPA filters just prior to the fan inlet. Discharge exhaust air above the highest roof level through a stack at least 10 ft [3 m] tall at 3,500 fpm [18 m/s] discharge velocity. The discharge air outlet shall be located at least 25 ft [8 m] from outdoor air intakes and operable windows. Follow the recommendations of the dispersion analysis for higher than minimum requirements. Provide emergency power for the exhaust fan and associated controls. Label ductwork, filter, and fan "COMMUNICABLE DISEASE CONTAMINATED AIR". Where ever practical connect as many AII rooms as possible to one exhaust system. In all cases provide two exhaust system and operate in LEAD/LAG configuration with automatic controls to turn on LAG fan upon LEAD fan failure. | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. AII Isolation Room. Locate the exhaust air inlet over or near the patient bed to ensure that air flows into the room and away from the patient room door. Preferred location of the exhaust air inlet is in the wall, 7 in [175 mm] above the floor, and near the patient head rest.
Protective Environment (PE) Positive Air Pressure | XXXXX | Protective Environment Ante Room | NA | NA | NA | NA | NA | NA | 10 | NA | Return | 35 | (+) | No | CV |  | Note 1 - Terminal HEPA Filter. Provide duct-mounted, terminal MERV 17 (HEPA) filter downstream of the dedicated air terminal units serving the Isolation Rooms. Ensure access for filter replacement and instrumentation. Provide a differential pressure gage and a differential pressure switch with a remote alarm to the ECC when the pressure drop exceeds the recommended pressure drop. | Note 2 - Instrumentation.Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. PE Ante Room. Air shall transfer from the Isolation Room into the Ante Room and then to the Corridor. The Ante Room is negative with respect to the Isolation Room and positive with respect to the Corridor.
Protective Environment (PE) Positive Air Pressure | XXXXX | Protective Environment Isolation Room | 75 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Return | 35 | (++) | Yes | CV |  | Note 1 - Terminal HEPA Filter. Provide duct-mounted, terminal MERV 17 (HEPA) filter downstream of the dedicated air terminal units serving the Isolation Rooms. Ensure access for filter replacement and instrumentation. Provide a differential pressure gage and a differential pressure switch with a remote alarm to the ECC when the pressure drop exceeds the recommended pressure drop. | Note 2 - Instrumentation.Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. PE Isolation Room. Locate the exhaust air inlet over or near the entry door to ensure that air flows into the room and away from the patient bed.
PATHOLOGY & LABORATORIES | [16 empty] | Note 1 - General: Coordinate supply and exhaust air volumes with the fume hoods and biological safety cabinets. A general exhaust system shall be provided where spaces are not equipped with fume hoods and/or biological safety cabinets.
PATHOLOGY & LABORATORIES | XXXXX | Bacteriology | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
PATHOLOGY & LABORATORIES | XXXXX | Biochemistry | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
PATHOLOGY & LABORATORIES | XXXXX | Cytology | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
PATHOLOGY & LABORATORIES | XXXXX | Dry Laboratories | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained. | Note 2 - Room air can be returned only if chemicals are not used in the room.
PATHOLOGY & LABORATORIES | XXXXX | Glass Washing | NA | NA | NA | NA | NA | NA | 10 | 2 | Exhaust (S) | 40 | (-) | No | CV |  | Note 1 - Wet Exhaust System. Provide a wet exhaust system.
PATHOLOGY & LABORATORIES | XXXXX | Histology | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV
PATHOLOGY & LABORATORIES | XXXXX | Media Transfer | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust (S) | 45 | (+) | Yes | CV |  | Note 1 - Room Air Returns. Room air can be returned if chemicals are not used in the room.
PATHOLOGY & LABORATORIES | XXXXX | Microbiology | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
PATHOLOGY & LABORATORIES | XXXXX | Pathology | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
PATHOLOGY & LABORATORIES | XXXXX | Serology | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
PATHOLOGY & LABORATORIES | XXXXX | Sterilizing | 75 | 24 | 70 | 21 | 60 | 30 | 10 | 2 | Exhaust (S) | 40 | (-) | Yes | CV or VAV |  | Note 1 - Wet Exhaust System. (a) Provide a wet exhaust system. (b) Where VAV supply is provided, an exhaust valve shall also be provided to ensure room balance is maintained.
MENTAL HEALTH INPATIENT | BRNP1 | One Bed Patient Room Standard/Accessible/Bariatric | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil unit and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers.
MENTAL HEALTH INPATIENT | TLTS2 | Patient Toilet Standard/Accessible/Bariatric | NA | NA | 68 | 20 | NA | 30 | 10 | NA | Exhaust (G) | 35 | (--) | Notes | CV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers. | Note 4 - Bathroom Exhaust. Bathroom shall be constantly exhausted at highest of 10 ACH rate, 50 CFM, or room air balance with the makeup air coming from the patient room thus maintaining the bathroom flow 30% negative to the patient room and the patient room neutral to the corridor; therefore the minimum outside air to the patient room shall be 2 ACH or the required bathroom makeup whichever is greater. | Note 5 - Bathroom Temperature. Bathrooms without heat loss do not required heating or cooling. Bathrooms with heat loss shall be provided with a supply diffuser from the room variable air volume terminal, or radiant heating which meets the safety requirements of note 1.
MENTAL HEALTH INPATIENT | BRNP2 | Two Bed Patient Room Standard | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers.
MENTAL HEALTH INPATIENT | TLTS2 | Patient Toilet Standard | NA | NA | 68 | 20 | NA | 30 | 10 | NA | Exhaust (G) | 35 | (--) | Notes | CV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers. | Note 4 - Bathroom Exhaust. Bathroom shall be constantly exhausted at highest of 10 ACH rate, 50 CFM, or room air balance with the makeup air coming from the patient room thus maintaining the bathroom flow 30% negative to the patient room and the patient room neutral to the corridor; therefore, the minimum outside air to the patient room shall be 2 ACH or the required bathroom makeup whichever is greater. | Note 5 - Bathroom Temperature. Bathrooms without heat loss do not required heating or cooling. Bathrooms with heat loss shall be provided with a supply diffuser from the room variable air volume terminal, or radiant heating which meets the safety requirements of note 1.
MENTAL HEALTH INPATIENT | BRNP5 | Isolation Restraint Room / Isolation Seclusion Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers.
MENTAL HEALTH INPATIENT | BRNP6 | Ante Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers.
MENTAL HEALTH INPATIENT | TLTS3 | Patient Toilet Standard | NA | NA | 68 | 20 | NA | 30 | 10 | NA | Exhaust (G) | 35 | (--) | Notes | CV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers. | Note 4 - Bathroom Exhaust. Bathroom shall be constantly exhausted at highest of 10 ACH rate, 50 CFM, or room air balance with the makeup air coming from the patient room thus maintaining the bathroom flow negative to the patient room and the patient room neutral to the corridor; therefore, the minimum outside air to the patient room shall be 2 ACH or the required bathroom makeup whichever is greater. | Note 5 - Bathroom Temperature. Bathrooms without heat loss do not required heating or cooling. Bathrooms with heat loss shall be provided with a supply diffuser from the room variable air volume terminal, or radiant heating which meets the safety requirements of note 1.
MENTAL HEALTH INPATIENT | NSTA1 | Nursing Station | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
MENTAL HEALTH INPATIENT | WRCH1 | Nurse Workroom | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
MENTAL HEALTH INPATIENT | MEDP1 | Medication Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
MENTAL HEALTH INPATIENT | CRA01 | Team Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
MENTAL HEALTH INPATIENT | FSCD1 | Dining Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | VAV |  | Note 1 - Local Exhaust Requirements. Provide general and / or local exhaust as required by ASHRAE 62.1-2016 or latest approved edition. Makeup air shall come from the Corridor.
MENTAL HEALTH INPATIENT | FSPT1 | Serving / Pantry | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (-) | Yes | VAV |  | Note 1 - Local Exhaust Requirements. Provide general and / or local exhaust as required by ASHRAE 62.1-2016 or latest approved edition. Makeup air shall come from the Dining Room.
MENTAL HEALTH INPATIENT | DAYR1 | Day Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
MENTAL HEALTH INPATIENT | OPMH1 | Group Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | BRAR2 | Suite Vestibule (Two Bedroom Suite) | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers. | Note 4 - Individual Temperature Control. Each bedroom in a two bedroom suite shall have individual temperature control and the vestibule shall be on the same controls as the accessible room. | Note 5 - Pressure Relationships and makeup air. The vestibule shall be neutral to the bedrooms and positive to the bathroom and shall provide enough makeup air to makeup all the bathroom exhaust.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | BRUN1 | One Bed Patient Room Standard / Accessible / Bariatric | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (0) | Yes | VAV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | TLTS2 | Patient Toilet Standard / Accessible / Bariatric | NA | NA | 68 | 20 | NA | 30 | 10 | NA | Exhaust (G) | 35 | (--) | Notes | CV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers. | Note 4 - Bathroom Exhaust. Bathroom shall be constantly exhausted at highest of 10 ACH rate, 50 CFM, or room air balance with the makeup air coming from the patient room thus maintaining the bathroom flow 30% negative to the patient room and the patient room neutral to the corridor; therefore, the minimum outside air to the patient room shall be 2 ACH or the required bathroom makeup whichever is greater. | Note 5 - Bathroom Temperature. Bathrooms without heat loss do not require heating or cooling. Bathrooms with heat loss shall be provided with a supply diffuser from the room variable air volume terminal, or radiant heating which meets the safety requirements of note 1.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | BRNC2 | Two Bed Patient Room Standard | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | TLTS2 | Patient Toilet Standard | NA | NA | 68 | 20 | NA | 30 | 10 | NA | Exhaust (G) | 35 | (--) | Notes | CV |  | Note 1 - Safety Requirements - Exposed Equipment. Use of exposed and accessible HVAC equipment is not permitted (examples: Room-mounted fan coil units and convectors, air outlets/inlets, temperature sensors, etc.). | Note 2 - Safety Requirements - Suspended Ceiling. Do not use lay-in tile acoustical ceiling. Use hard ceiling or concealed snap in arrangement. Keep ceiling height as high as possible. Use security clips to retain radiant ceiling panels in place. Ensure coordination with the architectural discipline. | Note 3 - Safety Requirements - Suspended Air Outlets/Inlets. Provide security diffusers, grilles, and registers. | Note 4 - Bathroom Exhaust. Bathroom shall be constantly exhausted at highest of 10 ACH rate, 50 CFM, or room air balance with the makeup air coming from the patient room thus maintaining the bathroom flow negative to the patient room and the patient room neutral to the corridor; therefore, the minimum outside air to the patient room shall be 2 ACH or the required bathroom makeup whichever is greater. | Note 5 - Bathroom Temperature. Bathrooms without heat loss do not require heating or cooling. Bathrooms with heat loss shall be provided with a supply diffuser from the room variable air volume terminal, or radiant heating which meets the safety requirements of note 1.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | DAYR1 | Living Area | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Safety Requirements. Comply with safety requirements indicated for patient rooms.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | FSCD1 | Dining Area | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Safety Requirements. Comply with safety requirements indicated for patient rooms.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | IPK01 | Kitchenette | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Safety Requirements. Comply with safety requirements indicated for patient rooms. | Note 2 - Local Exhaust Requirements. Provide general and / or local exhaust as required by ASHRAE 62.1-2016 or latest approved edition. Makeup air shall come from the Dining Area or Multi-Purpose Room as the case may be.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | DAYR1 | Resident Lounge | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Safety Requirements. Comply with safety requirements indicated for patient rooms.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | IPK01 | Multi-Purpose Room/Kitchenette | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Safety Requirements. Comply with safety requirements indicated for patient rooms. | Note 2 - Local Exhaust Requirements. Provide general and / or local exhaust in kitchenette as required by ASHRAE 62.1-2016 or latest approved edition. Makeup air shall come from the Dining Area or Multi-Purpose Room as the case may be. | Note 3 - Temperature Control. If the rooms are separated by walls or half walls with cased opening provide individual temperature control in Multi-Purpose Room and in Kitchenette, otherwise provide one control zone for both rooms with the sensor in the multi-purpose room.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | CRA02 | Resident Education/Conference/Group Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Safety Requirements. Comply with safety requirements indicated for patient rooms.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | FSCD1 | Dining Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Safety Requirements. Comply with safety requirements indicated for patient rooms. | Note 2 - Makeup Air Requirements. If provided with adjacent kitchen ensure this space has sufficient air to makeup kitchen exhaust.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | FSPT1 | Serving / Pantry | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Note 1 | 40 | Note 1 | Yes | VAV |  | Note 1 - Room Air Balance and Exhaust. Provide general and / or local exhaust as required by ASHRAE 62.1-2016 or latest approved edition, and / or by the equipment provided in the space. Makeup air shall come from the Dining Area. If exhaust is required the space shall be negative otherwise it shall be neutral. Return is permitted.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | IPK01 | Training Kitchen | 75 | 24 | 70 | 21 | 60 | NA | 6 | 2 | Exhaust G & S | 40 | (--) | Yes | CV |  | Note 1 - General. Space includes a pantry not requiring HVAC. | Note 2 - Outside Air Requirements. If this space is served by a dedicated air handling unit return air may be used. If the space is served by an air handling unit used for other occupied spaces then all air delivered to the kitchen shall be exhausted and no return shall be allowed. Adjust the minimum outside air for the air handling unit such that the entire system is at least 15% positive by flow, while maintaining the kitchen negative to its surroundings. | Note 3: - Kitchen Exhaust For Kitchens With Dedicated Air Handling Units. An NFPA 96 dedicated exhaust system shall serve hoods over cooking equipment. When the kitchen hood systems are off the exhaust system shall exhaust at least 2 air changes per hour and shall maintain the kitchen negative relative to its surroundings. | Note 4: - Kitchen Exhaust For Kitchens Without Dedicated Air Handling Units. An NFPA 96 dedicated exhaust system shall serve hoods over cooking equipment. Supplemental exhaust shall ensure the kitchen space is maintained negative to its surrounding during all occupied times regardless of whether or not the kitchen hoods are operating.
MENTAL HEALTH RESIDENTIAL REHABILITATION TREATMENT PROGRAM (RRTP) FACILITY | DAYR1 | Recreation Therapy Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Safety Requirements. Comply with safety requirements indicated for patient rooms.
MENTAL HEALTH OUTPATIENT SERVICES | EXRG3 | Exam Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Individual Room Temperature Control. Required for a single office. Otherwise see Chapter 2 for room temperature control requirements.
MENTAL HEALTH OUTPATIENT SERVICES | TRGM1 | Treatment Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Individual Room Temperature Control. Required for a single office. Otherwise see Chapter 2 for room temperature control requirements.
MENTAL HEALTH OUTPATIENT SERVICES | OPMH1 | Group Therapy Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
MENTAL HEALTH OUTPATIENT SERVICES | OPMH2 | Group Testing Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
MENTAL HEALTH OUTPATIENT SERVICES | OPMH3 | Biofeedback Laboratory Treatment Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
MENTAL HEALTH OUTPATIENT SERVICES | CMP02 | Biofeedback Laboratory Control Room / Office | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
MENTAL HEALTH OUTPATIENT SERVICES | OFD01 | Counselor Office | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
MENTAL HEALTH OUTPATIENT SERVICES | SL001 | Social Activities/ Dining/Multi-Purpose | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
MENTAL HEALTH OUTPATIENT SERVICES | CRA02 | Classroom / Group Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
MENTAL HEALTH OUTPATIENT SERVICES | OTGC1 | Occupational Therapy | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1: Dryer Exhaust. Coordinate clothes dryer exhaust with the actual machine used. | Note 2: Kiln Exhaust. Coordinate kiln exhaust with actual kiln used. Coordinate exhaust system design with NFPA 86 Standard for Ovens and Furnaces latest edition.
NURSING WING | BRIC1 | Patient Bedroom, Intensive Care | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+) | Yes | VAV |  | Note 1 - Filtration Requirements. For ICUs served by the Surgical Suite AHU, refer to the surgical AHU for terminal filtration requirements.
NURSING WING | XXXXX | Patient Bedroom | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+) | Yes | VAV
NURSING WING | XXXXX | Litter Bath | 82 | 28 | 70 | 21 | 60 | 30 | 15 | 2 | Exhaust (G) | 45 | (-) | Yes | VAV
NURSING WING | NSTA1 | Nurses Station | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
NURSING WING | BRII1 | Patient Room, Isolation (AII) | 75 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Exhaust (S) | 35 | (--) | Yes | CV |  | Note 1 - Special Exhaust System. See infectious isolation rooms/protective environment room data sheets for more information. Provide a dedicated, special exhaust system for the Patient Bedroom, Ante Room and Patient Toilet (where present). Do not connect other rooms to the dedicated exhaust system. Locate the exhaust fan at the end of the duct run to maintain the ductwork within the building at a negative pressure and install bag-in-bag out HEPA filters just prior to the fan inlet. Discharge exhaust air above the highest roof level through a stack at least 10 ft [3 m] tall at 3,500 fpm [18 m/s] discharge velocity. The discharge air outlet shall be located at least 25 ft [8 m] from outdoor air intakes and operable windows. Follow the recommendations of the dispersion analysis for higher than minimum requirements. Provide emergency power for the exhaust fan and associated controls. Label ductwork, filter, and fan "COMMUNICABLE DISEASE CONTAMINATED AIR". | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor.
NURSING WING | BRII2 | Patient Room, Isolation (PE) | 75 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Return | 35 | (++) | Yes | CV |  | Note 1 - Special Exhaust System. See infectious isolation rooms/protective environment room data sheets for more information. Provide a dedicated, special exhaust system for the Patient Bedroom, Ante Room and Patient Toilet (where present). Do not connect other rooms to the dedicated exhaust system. Locate the exhaust fan at the end of the duct run to maintain the ductwork within the building at a negative pressure and install bag-in-bag out HEPA filters just prior to the fan inlet. Discharge exhaust air above the highest roof level through a stack at least 10 ft [3 m] tall at 3,500 fpm [18 m/s] discharge velocity. The discharge air outlet shall be located at least 25 ft [8 m] from outdoor air intakes and operable windows. Follow the recommendations of the dispersion analysis for higher than minimum requirements. Provide emergency power for the exhaust fan and associated controls. Label ductwork, filter, and fan "COMMUNICABLE DISEASE CONTAMINATED AIR". | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor.
NURSING WING | MEDP1 | Medication Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | No | CV
NURSING WING | NCWD1 | Nourishment Station | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | No | CV
OIT MAIN COMPUTER ROOM | [16 empty] | Note 1 – General: The room names listed below are from the VA PG 18-9 Chapter 232 Revised October 3, 2016. The actual room layouts, equipment disposition, and the HVAC parameters may vary with the project scope of work.
OIT MAIN COMPUTER ROOM | ITAE1 | OIT IT Active Equipment | 81 | 27 | 64 | 18 | 60 | 30 | 2 | NA | Return | 45 | (+) | Yes | CV |  | Note 1 – Hot and Cold Aisle Distribution and Return. Provide under floor distribution and overhead returns taking advantage of cold and hot aisles with respect to equipment racks. | Note 2: - Ventilation. Total AC/HR based on cooling load and HVAC equipment capacity, calculate outside air per ASHRAE 62.1 -2016 or latest approved edition and provide (Option 1) from convenient nearby system or (Option 2) outside air ducted to CRAC inlet. | Note 3: - Relative Humidity. Recommended relative humidity requirements is dew point from 42F to 59 F.
OIT MAIN COMPUTER ROOM. | ITPE1 | OIT IT Passive Distribution Equipment | 81 | 27 | 64 | 18 | 60 | 30 | 2 | NA | Return | 45 | (+) | Yes | CV |  | Note 1 – Hot and Cold Aisle Distribution and Return. Provide under floor distribution and overhead returns taking advantage of cold and hot aisles with respect to equipment racks. | Note 2: - Ventilation. Total AC/HR based on cooling load and HVAC equipment capacity, calculate outside air per ASHRAE 62.1 -2016 or latest approved edition and provide (Option 1) from convenient nearby system or (Option 2) outside air ducted to CRAC inlet. | Note 3: - Relative Humidity. Recommended relative humidity requirements is dew point from 42F to 59 F.
OIT MAIN COMPUTER ROOM. | FMAE1 | FMS Active Equipment | 81 | 27 | 64 | 18 | 60 | 30 | 2 | NA | Return | 45 | (+) | Yes | CV |  | Note 1 – Hot and Cold Aisle Distribution and Return. Provide under floor distribution and overhead returns taking advantage of cold and hot aisles with respect to equipment racks. | Note 2: - Ventilation. Total AC/HR based on cooling load and HVAC equipment capacity, calculate outside air per ASHRAE 62.1 -2016 or latest approved edition and provide (Option 1) from convenient nearby system or (Option 2) outside air ducted to CRAC inlet. | Note 3: - Relative Humidity. Recommended relative humidity requirements is dew point from 42F to 59 F.
OIT MAIN COMPUTER ROOM. | FMPE1 | FMS Passive Distribution Equipment | 81 | 27 | 64 | 18 | 60 | 30 | 2 | NA | Return | 45 | (+) | Yes | CV |  | Note 1 – Hot and Cold Aisle Distribution and Return. Provide under floor distribution and overhead returns taking advantage of cold and hot aisles with respect to equipment racks. | Note 2: - Ventilation. Total AC/HR based on cooling load and HVAC equipment capacity, calculate outside air per ASHRAE 62.1 -2016 or latest approved edition and provide (Option 1) from convenient nearby system or (Option 2) outside air ducted to CRAC inlet. | Note 3: - Relative Humidity. Recommended relative humidity requirements is dew point from 42F to 59 F.
OIT MAIN COMPUTER ROOM. | TEIP1 | VoIP Active Equipment | 81 | 27 | 64 | 18 | 60 | 30 | 2 | NA | Return | 45 | (+) | Yes | CV |  | Note 1 – Hot and Cold Aisle Distribution and Return. Provide under floor distribution and overhead returns taking advantage of cold and hot aisles with respect to equipment racks. | Note 2: - Ventilation. Total AC/HR based on cooling load and HVAC equipment capacity, calculate outside air per ASHRAE 62.1 -2016 or latest approved edition and provide (Option 1) from convenient nearby system or (Option 2) outside air ducted to CRAC inlet. | Note 3: - Relative Humidity. Recommended relative humidity requirements is dew point from 42F to 59 F.
OIT MAIN COMPUTER ROOM. | ITAD1 | Storage Active Data Room | 81 | 27 | 64 | 18 | 60 | 30 | 2 | NA | Return | 45 | (+) | Yes | CV |  | Note 1 – Hot and Cold Aisle Distribution and Return. Provide under floor distribution and overhead returns taking advantage of cold and hot aisles with respect to equipment racks. | Note 2: - Ventilation. Total AC/HR based on cooling load and HVAC equipment capacity, calculate outside air per ASHRAE 62.1 -2016 or latest approved edition and provide (Option 1) from convenient nearby system or (Option 2) outside air ducted to CRAC inlet. | Note 3: - Relative Humidity. Recommended relative humidity requirements is dew point from 42F to 59 F.
OIT MAIN COMPUTER ROOM. | ITNT1 | Network Operation Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (0) | Yes | VAV |  | Note 1 – Distribution. Provide with distribution from CRAC for main computer room or from other system in the vicinity.
OIT MAIN COMPUTER ROOM. | ITBU1 | Backup Computer Room | 81 | 27 | 64 | 18 | 60 | 30 | 2 | NA | Return | 45 | (+) | Yes | CV |  | Note 1 – Dedicated HVAC System. When a backup computer room is authorized it will be located remote from the main computer room and may or may not have adjacent Network Operation Room and Storage Active Data Room. The backup computer room shall have a separate dedicated HVAC system meeting all the requirements indicated for the main computer room and its related spaces shown above.
OIT SATELLITE DATA / VOICE EQUIPMENT ROOMS | [16 empty] | Note 1 -General: The room names listed below are from the VA PG 18-9 Chapter 232 Revised October 3, 2016. The actual room layouts, equipment disposition, and the HVAC parameters may vary with the project scope of work.
OIT SATELLITE DATA / VOICE EQUIPMENT ROOMS. | TEDR1 | Demarcation Room (Demarc Room) | 81 | 27 | 64 | 18 | 60 | 30 | 2 | NA | Return | 45 | (+) | Yes | CV |  | Note 1 - Ventilation. Total ACH based on cooling load and HVAC equipment capacity, outside air per ASHRAE 62.1 -2016 or latest approved edition and provide as indicated in the air handling unit data sheet.
OIT SATELLITE DATA / VOICE EQUIPMENT ROOMS. |  | Telephone Equipment Room (TER) | 81 | 27 | 64 | 18 | 60 | 30 | 2 | NA | Return | 45 | (+) | Yes | CV |  | Note 1 - Ventilation. Total ACH based on cooling load and HVAC equipment capacity, outside air per ASHRAE 62.1 -2016 or latest approved edition and provide as indicated in the air handling unit data sheet.
OIT SATELLITE DATA / VOICE EQUIPMENT ROOMS. | TEOR1 | Telephone Operators Room (TOR) | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. Serve this space with any system suitable for offices spaces.
OIT SATELLITE DATA / VOICE EQUIPMENT ROOMS. | TETR1 | Telecommunications Room (TR) | 81 | 27 | 64 | 18 | 60 | 30 | 2 | NA | Return | 45 | (+) | Yes | CV |  | Note 1 - Ventilation. Total ACH based on cooling load and HVAC equipment capacity, outside air per ASHRAE 62.1 -2016 or latest approved edition and provide as indicated in the air handling unit data sheet.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS | EXOS1 | Audiology Office/Therapy Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS | PEHS1 | Audiometric | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 25 | (o) | Yes | VAV |  | Note 1 - Acoustic Booth. Coordinate the installation of the acoustic booth (if any) and its integral HVAC system with the architectural layout and building utilities. | Note 2 - Room Noise Level. Provide acoustic measures to maintain the design NC level.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS | LBVP1 | Blood Draw Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Bone Marrow Transplant Suite | XXXXX | Donors Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+ +) | Yes | CV |  | Note 1 - Terminal HEPA Filter. Provide duct-mounted, terminal MERV 17 (HEPA) filter downstream of the dedicated air terminal units serving the Donor, Patient and Recovery Rooms. Ensure access for filter replacement and instrumentation. Provide a differential pressure gage and a differential pressure switch with a remote alarm to the ECC when the pressure drop exceeds the recommended pressure drop. | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. (a) Donor Patient and Recovery Rooms. Locate the exhaust air inlet over or near the entry door to ensure that air flow into the room airway from the patient bed. (b) Ante Room. Air shall transfer from the Donor Patient and Recovery Rooms into the Ante Room and then to the Corridor. The Ante Room is negative with respect to the Donor, Patient and Recovery Rooms and positive with respect to the Corridor.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Bone Marrow Transplant Suite | XXXXX | Medication Preparation Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+ +) | Yes | CV |  | Note 1 - Terminal HEPA Filter. Provide duct-mounted, terminal MERV 17 (HEPA) filter downstream of the dedicated air terminal units serving the Donor, Patient and Recovery Rooms. Ensure access for filter replacement and instrumentation. Provide a differential pressure gage and a differential pressure switch with a remote alarm to the ECC when the pressure drop exceeds the recommended pressure drop. | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. (a) Donor Patient and Recovery Rooms. Locate the exhaust air inlet over or near the entry door to ensure that air flow into the room airway from the patient bed. (b) Ante Room. Air shall transfer from the Donor Patient and Recovery Rooms into the Ante Room and then to the Corridor. The Ante Room is negative with respect to the Donor, Patient and Recovery Rooms and positive with respect to the Corridor.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Bone Marrow Transplant Suite | XXXXX | Patient Rooms | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+ +) | Yes | CV |  | Note 1 - Terminal HEPA Filter. Provide duct-mounted, terminal MERV 17 (HEPA) filter downstream of the dedicated air terminal units serving the Donor, Patient and Recovery Rooms. Ensure access for filter replacement and instrumentation. Provide a differential pressure gage and a differential pressure switch with a remote alarm to the ECC when the pressure drop exceeds the recommended pressure drop. | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. (a) Donor Patient and Recovery Rooms. Locate the exhaust air inlet over or near the entry door to ensure that air flow into the room airway from the patient bed. (b) Ante Room. Air shall transfer from the Donor Patient and Recovery Rooms into the Ante Room and then to the Corridor. The Ante Room is negative with respect to the Donor, Patient and Recovery Rooms and positive with respect to the Corridor.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Bone Marrow Transplant Suite | XXXXX | Recovery Rooms | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+ +) | Yes | CV |  | Note 1 - Terminal HEPA Filter. Provide duct-mounted, terminal MERV 17 (HEPA) filter downstream of the dedicated air terminal units serving the Donor, Patient and Recovery Rooms. Ensure access for filter replacement and instrumentation. Provide a differential pressure gage and a differential pressure switch with a remote alarm to the ECC when the pressure drop exceeds the recommended pressure drop. | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. (a) Donor Patient and Recovery Rooms. Locate the exhaust air inlet over or near the entry door to ensure that air flow into the room airway from the patient bed. (b) Ante Room. Air shall transfer from the Donor Patient and Recovery Rooms into the Ante Room and then to the Corridor. The Ante Room is negative with respect to the Donor, Patient and Recovery Rooms and positive with respect to the Corridor.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Bone Marrow Transplant Suite | XXXXX | Ante Room for Donor, Patient and Recovery Rooms | NA | NA | NA | NA | NA | NA | 10 | NA | Return | 35 | (+ ) | No | CV |  | Note 1 - Terminal HEPA Filter. Provide duct-mounted, terminal MERV 17 (HEPA) filter downstream of the dedicated air terminal units serving the Donor, Patient and Recovery Rooms. Ensure access for filter replacement and instrumentation. Provide a differential pressure gage and a differential pressure switch with a remote alarm to the ECC when the pressure drop exceeds the recommended pressure drop. | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. (a) Donor Patient and Recovery Rooms. Locate the exhaust air inlet over or near the entry door to ensure that air flow into the room airway from the patient bed. (b) Ante Room. Air shall transfer from the Donor Patient and Recovery Rooms into the Ante Room and then to the Corridor. The Ante Room is negative with respect to the Donor, Patient and Recovery Rooms and positive with respect to the Corridor.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Bone Marrow Transplant Suite | XXXXX | Examination Rooms | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. The design parameters are applicable to all examination rooms not involving treatment and/or procedures. | Note 2 - Individual Room Temperature Control. Refer to Chapter 2 for the guidelines on the individual room temperature control.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Therapy Rooms | XXXXX | Hydrotherapy/Therapeutic Pool | 75 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Exhaust (G) | 45 | (-) | Yes | CV |  | Note 1 - Hydrotherapy/Therapeutic Pool Rooms. The reheat coil capacity shall be sized to maintain up to 82 F [28 C] space temperature for the two rooms. | Note 2 - Hydrotherapy/Therapeutic Pool. Provide a dedicated wet exhaust system.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Therapy Rooms | XXXXX | Kinesiotherapy | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Kinesiotherapy Pool Rooms. The reheat coil capacity shall be sized to maintain up to 82 F [28 C] space temperature for the two rooms.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Therapy Rooms | XXXXX | Occupational Therapy | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Therapy Rooms | XXXXX | Physical Therapy | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (-) | Yes | VAV
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Treatment Rooms | XXXXX | Chemotherapy | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 35 | (-) | Yes | CV
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS Treatment Rooms | OPDU1 | Dermatology | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Risk Assessment. Conduct risk assessment if the room is to be used for dermatological procedures design per Procedure Room (formerly Class A Operation) room on next page.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS | XXXXX | Phototherapy/Shower Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 35 | (o)/(-) | Yes | VAV |  | Note 1 - Phototherapy/Shower Room. Maintain negative air balance in the Shower Room and neutral air balance in the Phototherapy Room.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS | XXXXX | Tub Room | 75 | 24 | 70 | 21 | 60 | 30 | 10 | 2 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Reheat Coil Capacity. The reheat coil capacity shall be sized to maintain 86 F [30 C] space temperature.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS | OPPF1 | OPPF1: Ventilatory Test Room | 75 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Exhaust Grilles. Provide low level exhaust grilles 7 in [175 mm] above the finished floor.
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS | EYVF1 | EYVF1: Visual Field/ EYFC1: Photography Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS | XXXXX | Vital Signs Station | NA | NA | NA | NA | NA | NA | 4 | NA | Return | 35 | (o) | No | VAV
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS | OPCR1 | Orthopedic Clinic (Cast Room) | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | VAV
PATIENT EXAMINATION, TREATMENT, AND PROCEDURE ROOMS | XXXXX | Procedure Room (formerly Class A Operating) | 68 | 20 | 70 | 21 | 60 | 30 | 15 | 3 | Return | 35 | (+) | Yes | CV |  | Note 1 - Air Distribution. Provide overhead supply and return air distribution. | Note 2 - Procedure rooms (formerly Class A Operating Rooms) are rooms designated for the performance of procedures that do not meet the glossary definition of invasive procedure and may be performed outside the restricted area of a surgical suite but may require the use of sterile instruments or supplies. Local anesthesia and minimal and moderate sedation may be administered but special ventilation or scavenging equipment must not be required for anesthetic agents used in these room. | Note 3 - Minimum Filter Requirement. Provide MERV 7 and MERV 11 prefilters and MERV 14 after filter.
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD2 | Dispensing Station | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD2 | Controlled Substance Work Area Vault | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD2 | Secured Controlled Substance Dispensing | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD2 | Extemporaneous Repackaging | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD2 | Stat Counter | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | XXYYC | Drug Information Area | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD2 | Breakdown and Verification Receiving Area | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD2 | Inventory and Verification Receiving Area | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD1 | Prescription Receiving Window | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD2 | Prescription Filling and Assembly Area | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD2 | Prescription Dispensing Area | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | PHOD2 | Prescription Mail Out | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | OFDC2 | Consult Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient and Outpatient Pharmacy Work and Support Areas | XXYYC | Pharmacy Cache Area | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
PHARMACY SERVICE Outpatient Pharmacy Patient Areas | WTG15 | Waiting Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
PHARMACY SERVICE Pharmacy Education Program | OFA07 | Clinical Pharmacy Teaching Coordinator Workstation | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
PHARMACY SERVICE Pharmacy Education Program | XXYYC | Pharmaceutical Experimentation Laboratory | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust | 40 | (-) | Yes | VAV |  | Note 1 - Local Exhaust Hood. Provide dedicated exhaust system for fume hood or biological safety cabinet if one is provided. Coordinate exhaust and makeup air with selected hood.
PHARMACY SERVICE Pharmacy Education Program | OFA07 | Intern / Student Workstation | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
PHARMACY SERVICE Pharmacy Education Program | OFA10 | Trainee Carrel | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
PHARMACY SERVICE Inpatient Pharmacy Staff and Administration Areas | OFA09 | Pharmacy Service Chief Office / Associate Chief Office | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
PHARMACY SERVICE Inpatient Pharmacy Staff and Administration Areas | WTG03 | Waiting | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
PHARMACY SERVICE Inpatient Pharmacy Staff and Administration Areas | OFA07 | Pharmacist Workstation | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
PHARMACY SERVICE Inpatient Pharmacy Staff and Administration Areas | OFA07 | Secretary Workstation / Clerical Workstation | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
PHARMACY SERVICE Inpatient Pharmacy Staff and Administration Areas | CFR01 | Conference Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+) | Yes | VAV
PHARMACY SERVICE Inpatient Pharmacy Staff and Administration Areas | SL001 | Staff Lounge | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | VAV |  | Note 1 - Local Exhaust Hood and / or General Exhaust. Evaluate the level of cooking that may take place and design accordingly, for example if a range hood is being provided design the exhaust system for the hood.
PHARMACY SERVICE USP Chapter 797 and USP Chapter 800 Areas | [16 empty] | Note 1 - General Notes. (a) Room Names and Codes: There are two sets of room names presented in this section. First listed is the VA room code followed by the VA room name. These are consistent with the codes and names found in Chapter 268: Pharmacy Service in PG-18-9 Space Planning Criteria dated March 2008 and revised October 3, 2016. The second room name is consistent with the best available documents for USP 797 and USP 800 at the time this manual was revised. It is recommended that the USP 797 and USP 800 room names be used on the contract documents with the VA nomenclatures presented here only for reference. (b) USP 800: The information in this table is consistent with USP Chapter 800 Hazardous Drugs - Handling in Health Care Settings approved for public release on February 1, 2016 and scheduled for mandatory implementation on July 1, 2018. (c) USP 797: At the time this manual was being revised USP Chapter 797 Pharmaceutical Compounding - Sterile Preparations was out for public review and comments with a projected completion / publishing date of May 1, 2017. Hence the information used for this table is based on unpublished information. However, since the majority of the changes to USP chapter 797 are for the purpose of coordinating the chapter to the newly released USP Chapter 800 using both available documents at the time of manual re-writing gives high confidence that the information presented here is will be consistent with both final documents (USP 797 and USP 800). (d) Complexity: These Room Data Sheets should be considered only a starting point for the design of HVAC for USP 797 and USP 800 rooms. The A/E must be familiar with and must references both USP 797 and USP 800 when completing the design work to ensure all the complexities of these spaces are addressed. | Note 2 - Pressure Differentials. As a minimum maintain a pressure differential of 0.02 inches of water column between spaces of different cleanliness or of different chemical substance risk level. Provide visual indicators between the rooms so that workers can easily see that correct pressure levels are being maintained. | Note 3 - Air Terminals. Air terminals, reheat coils and their controls must be outside the clean spaces to facilitate maintenance without fouling the space. | Note 4 - Air Distribution. Provide unidirectional air distribution with overhead supply and bottom return air collection. Locate return air inlet(s) in the wall at 7 in [175 mm] above the floor. | Note 5 - Materials. Flexible ductwork must not be used in any of the supply and exhaust ducts serving these spaces. All exhaust ducts and all supply ducts downstream of HEPA filters must be welded stainless steel. | Note 6 - Monitoring. Provide visual and digital pressure display as well as digital temperature and relative humidity displays. Trend and alarm all measurements.
PHARMACY SERVICE USP Chapter 797 and USP Chapter 800 Areas | PHIV2 | Intravenous Admixture Anteroom or USP 797 Ante-areas | 68 | 20 | 68 | 20 | 60 | 30 | 25 | 15 | Return | 40 | (+) | Yes | CV |  | Note 1: General. This ISO Class 7 anteroom is a work room for preparation to do work in the buffer rooms. It is a space positive to areas outside the compounding suite and negative to the cleaner spaces within the compounding suite. Following the convention that doors shall swing into the cleaner spaces, the door into this room from outside the compounding suite shall swing into this room and doors from this room to cleaner spaces shall swing out of this room. This room must be equipped with touchless hand washing and dryer equipment. | Note 2: Dual Purpose Ante Room. One ante room may be used to serve both an oncology drug buffer room and a non-oncology drug buffer room. In that case the ante room would have 100% outside air pass through (100% exhaust less exfiltration to keep space pressurized). In all cases an ante room is needed for the oncology buffer.
PHARMACY SERVICE USP Chapter 797 and USP Chapter 800 Areas | PHOD2 | Oncology Drug Intravenous Admixture Anteroom or USP 797 or USP 800 Ante-areas | 68 | 20 | 68 | 20 | 60 | 30 | 35 | 35 | Exhaust | 40 | (+) | Yes | CV |  | Note 1: General. This ISO Class 7 anteroom is a work room for preparation to do work in the buffer rooms. It is a space positive to areas outside the compounding suite and negative to the cleaner spaces within the compounding suite. Following the convention that doors shall swing into the cleaner spaces, the door into this room from outside the compounding suite shall swing into this room and doors from this room to cleaner spaces shall swing out of this room. This room must be equipped with touchless hand washing and dryer equipment. | Note 2: Dual Purpose Ante Room. One ante room may be used to serve both an oncology drug buffer room and a non-oncology drug buffer room. In that case the ante room would have 100% outside air pass through (100% exhaust less exfiltration to keep space pressurized). In all cases an ante room is needed for the oncology buffer.
PHARMACY SERVICE USP Chapter 797 and USP Chapter 800 Areas | PHIV2 | Intravenous Admixture Aseptic Transfer Room or USP 797 Buffer | 68 | 20 | 68 | 20 | 60 | 30 | 35 | 15 | Return | 40 | (+) | Yes | CV |  | Note 1: General. This ISO Class 7 work area is the area in which the IV admixture work takes place. Inside this space will be placed the Primary Engineering Controls (PEC) which in most cases is an ISO Class 5 laminar flow bench. The admixture work takes place in the PEC. | Note 2: Pressure Relationships. (a) Non-Oncology Buffer: This space must be maintained at least 0.02 inches of water column positive with respect to the ante area. (b) Oncology Buffer Area: This space must be maintained -0.01 to 0.03 inches of water column negative with respect to the ante area or any other area adjacent to it. | Note 3: Exhaust System. Provide exhaust system for the primary engineering control, maintain ductwork negative by placing the fan at the end of the duct run and discharge in a location as discussed in Chapter 3 to prevent contamination of building air intakes. The exhaust for the primary engineering control must vented through a HEPA filter system.
PHARMACY SERVICE USP Chapter 797 and USP Chapter 800 Areas | PHOD2 | Oncology Drug Preparation Area or USP 800 Buffer | 68 | 20 | 68 | 20 | 60 | 30 | 35 | 35 | Exhaust | 40 | (-) | Yes | CV |  | Note 1: General. This ISO Class 7 work area is the area in which the IV admixture work takes place. Inside this space will be placed the Primary Engineering Controls (PEC) which in most cases is an ISO Class 5 laminar flow bench. The admixture work takes place in the PEC. | Note 2: Pressure Relationships. (a) Non-Oncology Buffer: This space must be maintained at least 0.02 inches of water column positive with respect to the ante area. (b) Oncology Buffer Area: This space must be maintained -0.01 to 0.03 inches of water column negative with respect to the ante area or any other area adjacent to it. | Note 3: Exhaust System. Provide exhaust system for the primary engineering control, maintain ductwork negative by placing the fan at the end of the duct run and discharge in a location as discussed in Chapter 3 to prevent contamination of building air intakes. The exhaust for the primary engineering control must vented through a HEPA filter system. | Note 4 - Air Changes Per Hour. Air changes per hour are required to be derived from HEPA filtered air supplied to the space.
PHARMACY SERVICE USP Chapter 797 and USP Chapter 800 Areas | XXXXX | USP 800 Anteroom for Oncology Buffer | NA | NA | NA | NA | NA | NA | 35 | 35 | Exhaust | 40 | (+) | No | CV |  | Note 1: General. Although it is not a requirement, this space is intended to meet two requirements in USP 797 (1): Air from the oncology buffer must not transfer to other occupied spaces and (2): Air from an ISO 8 space must not transfer into ISO 7 space. Therefore, the Anteroom is designed and maintained at ISO 7 conditions and positive to the buffer and to the ante space. Its function is to keep the oncology buffer clean with its potentially hazardous conditions (spill, evaporating etc.) contained. There are other alternatives to this space discussed in USP 800. | Note 2: Pressure Relationships. This space must be maintained at least 0.04 inches of water column positive with respect to the ante area and 0.02 inches of water column positive with respect to the oncology buffer.
PHARMACY SERVICE USP Chapter 797 and USP Chapter 800 Areas | PHBS2 | Storage and Clean / Decontamination Area or USP 800 Unpacking / Storage Hazardous Drugs | 68 | 20 | 68 | 20 | 60 | 30 | 12 | 12 | Exhaust | 40 | (-) | Yes | CV |  | Note 1: General. Unpacking from shipping containers shall not take place in areas used for sterile compounding nor in areas used to store or unpack non-hazardous drugs. Storage of HD shall not be in the same storage as non HD. | Note 2: Venting of Containment - Primary Engineering Control. If a containment primary engineering control is provided in this space, provide exhaust system for the primary engineering control, maintain ductwork negative by placing the fan at the end of the duct run and discharge in a location as discussed in Chapter 3 to prevent contamination of building air intakes. The exhaust for the primary engineering control must vented through a HEPA filter system. | Note 3 - Air Changes Per Hour. Air changes per hour are required to be derived from HEPA filtered air supplied to the space.
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | BRSM1 | Patient Bedroom | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | TSPP1 | Patient Toilet / Shower | NA | NA | 68 | 20 | NA | NA | 10 | NA | Exhaust (G) | 35 | (-) | No | CV |  | Note 1 - Bathroom Temperature. Bathrooms with heat loss shall be provided with diffuser from room terminal or preferably with radiant heating. | Note 2 - Bathroom Exhaust and Makeup Air. Bathrooms shall be constantly exhausted at a minimum of 10 ACH per hour and shall be maintained negative under all load conditions. Makeup air shall be from the patient room. The patient room shall be neutral to the corridor and positive to the bathroom.
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | NSTA1 | Inpatient Nurse Station | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | RCA01 | Crash Cart Alcove | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | No | NA |  | Note 1 - General. If crash cart alcove is exposed to heat loss or gain provide the space with a diffuser from the terminal serving the nurse station to offset the loads.
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | MEDP1 | Medication Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | PRD01 | Dining Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | VAV |  | Note 1: Dining Room Exhaust. Provide general exhaust to maintain space negative and to meet ASHRAE 62.1-2016 or latest approved edition requirements. The remainder of the supply can be returned to the air handling unit.
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | SRE01 | Food Pantry Storage | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | IPK01 | OT Training Kitchen | 75 | 24 | 70 | 21 | 60 | NA | 6 | 2 | Return | 40 | (-) | Yes | CV |  | Note 1: Kitchen Exhaust. Provide general exhaust to maintain space negative. The remainder of the supply can be returned to the air handling unit. If a range hood is provided, design exhaust per NFPA 96 latest edition at the time of design. Ensure general exhaust by itself is adequate to maintain the space negative even if the hood exhaust is off.
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | CLR09 | Family Wellness Multipurpose Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | PLAY1 | Playroom | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | LAUN1 | Patient Laundry Room | 78 | 26 | 70 | 21 | 60 | NA | 10 | 2 | Exhaust (G) | 45 | (-) | Yes | CV |  | Note 1 - Exhaust Provide dryer exhaust and coordinate with actual equipment used. General exhaust shall maintain the space negative and at minimum 10 ACH when the dryer exhaust is not in use.
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | PRGY1 | Rehabilitation Therapy Gym | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (-) | Yes | VAV |  | Note 1 - Exhaust. Maintain minimum required exhaust per ASHRAE Standard 62.1-2016 or latest approved edition and ensure space is minimum 15% negative under all load conditions.
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | PREV1 | PT/OT Evaluation Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | WRTM1 | Team Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | PRRT1 | Recreation Therapy Group Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. Evaluate planned activities that may require the space to be negative or may require local or general exhaust.
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | PRNT1 | Neuropsychology Testing Lab | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | PRTM1 | BROS Treatment/Office | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | PRAT1 | Assistive Technology Lab | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | PRRE1 | Rehabilitation Engineering Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust (G) | 45 | (-) | Yes | CV |  | Note 1 - Rehabilitation Engineering Room. In addition to 100% exhaust from this space evaluate the need for local contaminant source exhaust.
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | SRS01 | Assistive Technology Equipment Storage | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | No | VAV |  | Note 1 - Temperature Control in Assistive Technology Equipment Storage. Provide temperature control only if required by Chapter 2. Otherwise provide cooling and heating from the Rehabilitation Engineering Room VAV terminal.
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | EXOS1 | Speech Language Pathologist Office | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Inpatient Nursing Unit | OFD05 | Provider Office | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | BRPT3 | Resident Bedroom | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | TSPB1 | Resident Toilet/Shower | NA | NA | 70 | 21 | NA | NA | 10 | NA | Exhaust (G) | 40 | (-) | No | CV |  | Note 1 - Bathroom Temperature. Bathrooms with heat loss shall be provided with diffuser from room terminal or preferably with radiant heating. | Note 2 - Bathroom Exhaust and Makeup Air. Bathrooms shall be constantly exhausted at a minimum of 10 ACH per hour and shall be maintained negative under all load conditions. Makeup air shall be from the patient room. The patient room shall be neutral to the corridor and positive to the bathroom.
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | PRAP1 | Apartment Living Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | BRPT1 | Apartment Bedroom | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | BTPU1 | Apartment Bathroom | NA | NA | 70 | 21 | NA | NA | 10 | NA | Exhaust (G) | 40 | (-) | No | CV |  | Note 1 - Bathroom Temperature. Bathrooms with heat loss shall be provided with diffuser from room terminal or preferably with radiant heating. | Note 2 - Bathroom Exhaust and Makeup Air. Bathrooms shall be constantly exhausted at a minimum of 10 ACH per hour and shall be maintained negative under all load conditions. Makeup air shall be from the patient room. The patient room shall be neutral to the corridor and positive to the bathroom.
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | PRCO3 | Apartment Kitchenette/Laundry | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust (G) | 40 | (-) | Note 1 | VAV |  | Note 1 - Kitchenette / Laundry Temperature Control. When consistent with good engineering practice based on load profiles, the kitchenette / laundry may be placed on the same temperature control zone as the living room. | Note 2 - Kitchenette / Laundry Exhaust. Provide dryer exhaust system. Coordinate with equipment to be used. Provide NFPA 96 kitchen hood exhaust system in the design and coordinate with equipment to be used.
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | SRE01 | Apartment Storage | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | NSTA6 | Transitional Rehabilitation Nurse Station | 75 | 24 | 70 | 21 | 6 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | MEDP1 | Medication Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | RCA01 | Crash Cart Alcove | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | No | NA |  | Note 1 - General. If crash cart alcove is exposed to heat loss or gain provide the space with a diffuser from the terminal serving the nurse station to offset the loads.
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | DAYR1 | Resident Living Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | PRD01 | Resident Dining Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | VAV |  | Note 1: Dining Room Exhaust. Provide general exhaust to maintain space negative to corridor and to meet ASHRAE 62.1-2016 or latest approved edition requirements. The remainder of the supply can be returned to the air handling unit. Note this space shall be positive to the kitchen.
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | PRK01 | Resident Kitchen | 75 | 24 | 70 | 21 | 60 | NA | 6 | 2 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1: Kitchen Exhaust. Provide NFPA 96 compliant exhaust system for cooking equipment and provide general exhaust as required to ensure the space is 100% exhausted even when kitchen equipment is not being operated.
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | PRGY2 | Rehabilitation Therapy Gym | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 35 | (-) | Yes | VAV |  | Note 1 - Exhaust. Maintain minimum required exhaust per ASHRAE Standard 62.1-2016 or latest approved edition and ensure space is minimum 15% negative under all load conditions.
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | PRAT2 | Assistive Technology Lab | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Polytrauma Transitional Rehabilitation Program | SRS01 | Assistive Technology Equipment Storage | NA | NA | NA | NA | NA | NA | NA | NA | Return | 45 | (o) | No | VAV |  | Note 1 - General. If equipment storage is exposed to heat loss or gain provide the space with a diffuser from the terminal serving the nurse station to offset loads.
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | EXRG0 | Outpatient Exam Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Note 1 | VAV |  | Note 1 - Temperature Control. If a single exam room is provided it shall have local temperature control. If more than one exam room see applicable sections of Chapter 2.
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PTEM1 | EMG Exam Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Note 1 | VAV |  | Note 1 - Temperature Control. If a single exam room is provided it shall have local temperature control. If more than one exam room see applicable sections of Chapter 2.
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PTBT1 | Chiropractic Exam Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Note 1 | VAV |  | Note 1 - Temperature Control. If a single exam room is provided it shall have local temperature control. If more than one exam room see applicable sections of Chapter 2.
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PRP01 | Pain Procedure Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PRDT1 | Driver Training Room | 70 | 21 | 65 | 18 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PTGL1 | Gait Observation Lab | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | SRE01 | Gait Lab Storage Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | NA | Return | 40 | (+) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PREX1 | Gait Lab Exam Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PRGY3 | Patient Rehabilitation Therapy Gym | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (-) | Yes | VAV |  | Note 1 - Exhaust. Maintain minimum required exhaust per ASHRAE Standard 62.1-2016 or latest approved edition and ensure space is minimum 15% negative under all load conditions.
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PRST1 | Speech Therapy Lab | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PRN01 | Balance Testing Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PRV01 | Vestibular Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | OFDC2 | Cognitive Therapy / Counseling Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
POLYTRAUMA REHABILITATION CENTER Outpatient Unit | PRRT2 | Recreational Therapy Group Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
PULMONARY MEDICINE SERVICE Procedure Room | OPPF1 | Pulmonary Function Testing Laboratory | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. l: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Pulmonary Medicine Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific pulmonary medicine service department warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Pulmonary Medicine Service AHU sheet and space requirements in the room data sheets (RDS) may be used. | Note 3 - Sputum Collection. Induced sputum collection should be preformed in a negative pressure room appropriate for that purpose.
PULMONARY MEDICINE SERVICE Procedure Room | OPPF2 | Extended Pulmonary Function Testing Laboratory | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. l: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Pulmonary Medicine Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific pulmonary medicine service department warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Pulmonary Medicine Service AHU sheet and space requirements in the room data sheets (RDS) may be used. | Note 3 - Sputum Collection. Induced sputum collection should be preformed in a negative pressure room appropriate for that purpose.
PULMONARY MEDICINE SERVICE Procedure Room | OPPF5 | Pulmonary Exercise Physiology Laboratory | 75 | 24 | 70 | 21 | 60 | 30 | 10 | 2 | Exhaust (G) | 40 | (-) | Yes | VAV |  | Note 1 - General. l: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Pulmonary Medicine Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific pulmonary medicine service department warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Pulmonary Medicine Service AHU sheet and space requirements in the room data sheets (RDS) may be used. | Note 3 - Sputum Collection. Induced sputum collection should be preformed in a negative pressure room appropriate for that purpose.
PULMONARY MEDICINE SERVICE Procedure Room | OPRT1 | Respiratory Therapy Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. l: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Pulmonary Medicine Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific pulmonary medicine service department warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Pulmonary Medicine Service AHU sheet and space requirements in the room data sheets (RDS) may be used. | Note 3 - Sputum Collection. Induced sputum collection should be preformed in a negative pressure room appropriate for that purpose.
PULMONARY MEDICINE SERVICE Procedure Room | OPRT1 | Aerosolized Pentamidine Room | 76 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - General. l: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Pulmonary Medicine Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific pulmonary medicine service department warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Pulmonary Medicine Service AHU sheet and space requirements in the room data sheets (RDS) may be used. | Note 3 - Sputum Collection. Induced sputum collection should be preformed in a negative pressure room appropriate for that purpose.
PULMONARY MEDICINE SERVICE Procedure Room | TRPE2 | Bronchoscopy Procedure Room | 76 | 20 | 70 | 21 | 60 | 30 | 12 | 2 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - General. l: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Pulmonary Medicine Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific pulmonary medicine service department warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Pulmonary Medicine Service AHU sheet and space requirements in the room data sheets (RDS) may be used. | Note 3 - Sputum Collection. Induced sputum collection should be preformed in a negative pressure room appropriate for that purpose.
PULMONARY MEDICINE SERVICE Procedure Room | OPPF6 | Sleep Study Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - General. l: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Pulmonary Medicine Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific pulmonary medicine service department warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Pulmonary Medicine Service AHU sheet and space requirements in the room data sheets (RDS) may be used. | Note 3 - Sputum Collection. Induced sputum collection should be preformed in a negative pressure room appropriate for that purpose.
PULMONARY MEDICINE SERVICE Procedure Room | OPPF7 | Sleep Study Monitor Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. l: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Pulmonary Medicine Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific pulmonary medicine service department warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Pulmonary Medicine Service AHU sheet and space requirements in the room data sheets (RDS) may be used. | Note 3 - Sputum Collection. Induced sputum collection should be preformed in a negative pressure room appropriate for that purpose.
PULMONARY MEDICINE SERVICE Procedure Room | RRSS1 | Patient Prep and Recovery | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - General. l: The space types listed in this manual reflect the terminology and functions used in the Department of Veterans Affairs, Pulmonary Medicine Service Design Guide dated November 29, 2011. | Note 2 - Air Handling Unit. If the size and / or arrangement of a specific pulmonary medicine service department warrants it, a separate air handling unit may be provided for this function, in general, however, any air handling unit meeting the minimum requirements of the Pulmonary Medicine Service AHU sheet and space requirements in the room data sheets (RDS) may be used. | Note 3 - Sputum Collection. Induced sputum collection should be preformed in a negative pressure room appropriate for that purpose.
R&D Common Back Area | SB241 | R&D Gas Manifold Room, Bldg Sprt | NA | NA | NA | NA | NA | NA | 6 | NA | Exhaust (G) | 40 | (- -) | No | CV | 6 | Note 1 - Room Exhaust. Transfer air from adjoining spaces for exhaust. Do not supply air under positive air pressure. Locate exhaust intakes within 12 inches of the floor.
R&D Common Back Area | SB244 | R&D Housekeeping Aides Closet (HAC), Bldg Sprt | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV
R&D Common Back Area | SB267 | R&D Recycling Room, Bldg Sprt | NA | NA | NA | NA | NA | NA | 4 | 4 | Exhaust (G) | 40 | (o) | No | CV |  | Note 1 - Room Supply. Air Provide a ducted, supply air takeoff from an adjoining air terminal unit.
R&D Common Back Area | SB551 | R&D Full / Empty Gas Cylinder Storage Room, Lgstcs Svc | NA | NA | NA | NA | NA | NA | 6 | NA | Exhaust (G) | 40 | (- -) | No | CV | 6 | Note 1 - Room Exhaust. Transfer air from adjoining spaces for exhaust. Do not supply air under positive air pressure. Locate exhaust intakes within 12 inches of the floor.
R&D Common Back Area | SB561 | R&D Flammable Storage Room, Lgstcs Svc | NA | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (S) | 40 | (- -) | No | CV |  | Note 1 - Exhaust System. Provide a dedicated exhaust system. Locate exhuast intakes within 12 inches of the floor. Exhaust to discharge directly to the building exterior. Comply with NFPA 30.
R&D Common Back Area | SB565 | R&D Corrosive Storage Room, Lgstcs Svc | NA | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (S) | 40 | (- -) | No | CV |  | Note 1 - Exhaust System. Provide a dedicated exhaust system. Terminate exhaust at least 10 ft. [3 m] above the highest roof level. Discharge exhaust at 3,500 fpm [18 m/s] and/or according to the dispersion analysis recommendations. Evaluate the need for filtration in the exhaust air duct before discharging outdoors. Consult with the end users and local safety officer for exhaust air filtration requirements.
R&D Common Back Area | SB687 | R&D Receiving Room, Lgstcs Svc | NA | NA | 60 | 15 | NA | NA | NA | NA | Return | 45 | (o) | Yes | CV |  | Note 1 - Heating System. Provide an air curtain with a heating element. Interlock the air curtain start with the loading dock door operating mechanism. Activate heating when the ambient temperature drops below 45 F [7 C] temperature.
R&D Common Back Area | SB773 | R&D Conference / Multipurpose Storage Room, Lgstcs Svc | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - General. This is a small closet and does not require HVAC.
R&D Common Back Area | SC816 | R&D Flex Storage, R&D, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
R&D Common Back Area | SC821 | Chemical Waste Room, R&D | NA | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (S) | 40 | (- -) | No | CV |  | Note 1 - Exhaust System. Provide a dedicated exhaust system. Terminate exhaust at least 10 ft. [3 m] above the highest roof level. Discharge exhaust at 3,500 fpm [18 m/s] and/or according to the dispersion analysis recommendations. Evaluate the need for filtration in the exhaust air duct before discharging outdoors. Consult with the end users and local safety officer for exhaust air filtration requirements.
R&D Common Back Area | SC822 | Radioactive Waste Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 10 | 2 | Exhaust (G) | 40 | (-) | Yes | VAV |  | Note 1 - Air Balance. Provide volumetric controls to demonstrate negative air balance.
R&D Common Back Area | SC823 | Biological Waste Room, R&D | NA | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (S) | 40 | (- -) | No | CV |  | Note 1 - Exhaust System. Provide a dedicated exhaust system. Terminate exhaust at least 10 ft. [3 m] above the highest roof level. Discharge exhaust at 3,500 fpm [18 m/s] and/or according to the dispersion analysis recommendations. Evaluate the need for filtration in the exhaust air duct before discharging outdoors. Consult with the end users and local safety officer for exhaust air filtration requirements.
R&D Common Back Area | SS101 | R&D Conference / Multipurpose Room, Educ Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1.
R&D Common Back Area | SS204 | R&D Administrative Officer (AO) Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
R&D Common Back Area | SS204 | R&D Administrative Chief of Staff (ACOS) Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
R&D Common Back Area | SS204 | R&D Research Compliance Officer (RCO) Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
R&D Common Back Area | SS262 | R&D Breakdown, Lgstcs Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
R&D Common Back Area | SS268 | R&D Copy / Supply Alcove, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
R&D Common Front Area | SB091 | R&D Contact / Information Station, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | CV
R&D Common Front Area | SB191 | R&D Visitor Universal Toilet, Bldg Sprt | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV
R&D Common Front Area | SB851 | R&D Security Station, Police Svc | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | ( o ) | Yes | VAV
R&D Common Front Area | SS222 | R&D Waiting, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
R&D Non-Profit (N-P) | SC814 | N-P Office Storage Room, R&D | NA | NA | 50 | 10 | NA | NA | NA | NA | NA | 40 | ( o ) | Yes | NA |  | Note 1 - Temperature Control. Storage rooms subject to heat loss shall be heated through a thermostatically controlled terminal unit.
R&D Non-Profit (N-P) | SS204 | R&D N-P Director Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
R&D Non-Profit (N-P) | SS204 | R&D N-P Executive Director Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
R&D Non-Profit (N-P) | SS218 | R&D N-P Staff Workstation, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
R&D Non-Profit (N-P) | SS221 | R&D N-P Reception, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
R&D Non-Profit (N-P) | SS222 | R&D N-P Waiting, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
R&D Non-Profit (N-P) | SS268 | R&D N-P Copy / Supply Alcove, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SB202 | RR&D Female Staff Toilet, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Rehabilitation Research & Development Unit (RRDU) | SB203 | RR&D Male Staff Toilet, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Rehabilitation Research & Development Unit (RRDU) | SB244 | RR&D Housekeeping Aides Closet (HAC), Bldg Sprt | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV
Rehabilitation Research & Development Unit (RRDU) | SB653 | RR&D Mailroom, Lgstcs Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SB773 | RR&D Conference / Multipurpose Storage Room, Lgstcs Svc | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - General. This is a small closet (80 SF) and does not require HVAC.
Rehabilitation Research & Development Unit (RRDU) | SC715 | RR&D Research Informatics Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SC727 | RR&D Patient Interview Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SC728 | RR&D Exam Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Note 1 | VAV |  | Note 1 - Temperature Control. If a single exam room is provided it shall have local temperature control. If more than one exam room see applicable sections of Chapter 2.
Rehabilitation Research & Development Unit (RRDU) | SC811 | RR&D Records Storage Room, R&D | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SS101 | RR&D Conference / Multipurpose Room, Educ Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1.
Rehabilitation Research & Development Unit (RRDU) | SS204 | RR&D PI Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
Rehabilitation Research & Development Unit (RRDU) | SS211 | RR&D Touch-Down Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SS212 | RR&D Collaboration Station, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SS216 | RR&D Trainee Workstation, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SS218 | RR&D Researcher Workstation, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SS221 | RR&D Reception, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SS222 | RR&D Waiting, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SS224 | RR&D Private Call Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1.
Rehabilitation Research & Development Unit (RRDU) | SS229 | RR&D Coat Closet, Stff Sprt | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - General. This is a small closet and does not require HVAC.
Rehabilitation Research & Development Unit (RRDU) | SS232 | RR&D Female Staff Locker Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Rehabilitation Research & Development Unit (RRDU) | SS241 | RR&D Male Staff Locker Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Rehabilitation Research & Development Unit (RRDU) | SS262 | RR&D Staff Breakroom, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air. Return air is permitted if the lounge is not equipped with vending machines, microwave, refrigerator, etc., otherwise follow requirements in ASHRAE Standard 62.1.
Rehabilitation Research & Development Unit (RRDU) | SS268 | RR&D Copy / Supply Alcove, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
Rehabilitation Research & Development Unit (RRDU) | SS285 | RR&D Huddle Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1.
Rehabilitation Research & Development Unit (RRDU) | SV692 | RR&D Vending Alcove, VC Svc | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Acute Care Unit Patient Area and Long Term Care Unit Patient Area | BRMS1 | One-Bed Patient Room | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 -Total Air Changes Per Hour & Negative Air Balance. Unlike other patient room / patient bathroom combinations these bathrooms will only get part of the makeup air from the patient bathroom. Each bathroom shall have its own constant volume temperature control terminal which shall provide enough makeup air to keep the bathroom negative relative to the patient room. | Note 2 - Energy Conservation Initiative. Include occupied / unoccupied mode of operation to conserve energy by analyzing the cost effectiveness of such features as occupancy sensors, two position supply air control, two position exhaust air control, and variable outside air control at the air handling unit.
SPINAL CORD INJURY/DISORDERS CENTER Acute Care Unit Patient Area and Long Term Care Unit Patient Area | BRMS2 | Two-Bed Patient Room | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 -Total Air Changes Per Hour & Negative Air Balance. Unlike other patient room / patient bathroom combinations these bathrooms will only get part of the makeup air from the patient bathroom. Each bathroom shall have its own constant volume temperature control terminal which shall provide enough makeup air to keep the bathroom negative relative to the patient room. | Note 2 - Energy Conservation Initiative. Include occupied / unoccupied mode of operation to conserve energy by analyzing the cost effectiveness of such features as occupancy sensors, two position supply air control, two position exhaust air control, and variable outside air control at the air handling unit.
SPINAL CORD INJURY/DISORDERS CENTER Acute Care Unit Patient Area and Long Term Care Unit Patient Area | TSPS1 | Patient Bathroom | 75 | 24 | 70 | 21 | NA | NA | 15 | NA | Exhaust G | 40 | (--) | Yes | CV |  | Note 1 -Total Air Changes Per Hour & Negative Air Balance. Unlike other patient room / patient bathroom combinations these bathrooms will only get part of the makeup air from the patient bathroom. Each bathroom shall have its own constant volume temperature control terminal which shall provide enough makeup air to keep the bathroom negative relative to the patient room. | Note 2 - Energy Conservation Initiative. Include occupied / unoccupied mode of operation to conserve energy by analyzing the cost effectiveness of such features as occupancy sensors, two position supply air control, two position exhaust air control, and variable outside air control at the air handling unit.
SPINAL CORD INJURY/DISORDERS CENTER Acute Care Unit Patient Area and Long Term Care Unit Patient Area | BRIT1 | Negative Pressure Isolation Patient Room (AII) | 72 | 22 | 82 | 28 | 60 | 30 | 12 | 2 | Exhaust (S) | 35 | (--) | Yes | CV |  | Note 1 - Special Exhaust System . Provide a dedicated, special exhaust system for the Patient Bedroom, Ante Room and Patient Toilet (where present). Do not connect other rooms to the dedicated exhaust system. Locate the exhaust fan at the end of the duct run to maintain the ductwork within the building at a negative pressure and install bag-in-bag out HEPA filters just prior to the fan inlet. Discharge exhaust air above the highest roof level through a stack at least 10 ft [3 m] tall at 3,500 fpm [18 m/s] discharge velocity. The discharge air outlet shall be located at least 25 ft [8 m] from outdoor air intakes and operable windows. Follow the recommendations of the dispersion analysis for higher than minimum requirements. Provide emergency power for the exhaust fan and associated controls. Label ductwork, filter, and fan "COMMUNICABLE DISEASE CONTAMINATED AIR". | Note 2 - Instrumentation.Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. (a) Patient Bedroom. Locate the exhaust air inlet over or near the patient bed to ensure that air flows into the room and away from the patient room door. Preferred location of the exhaust air inlet is in the wall, 7 in [175 mm] above the floor, and near the patient head rest. (b) Ante Room. Air shall transfer from the Corridor into the Ante Room and then to the Isolation Room. The Ante Room is positive with respect to the Isolation Room and negative with respect to the Corridor. | Note 4 -Toilet Room Total Air Changes Per Hour & Negative Air Balance. Unlike other patient room / patient bathroom combinations these bathrooms will only get part of the makeup air from the patient bathroom. Each bathroom shall have its own constant volume temperature control terminal which shall provide enough makeup air to keep the bathroom a minimum of 30% negative relative to the patient room. | Note 5 - Additional Information. See room data sheets (RDS) for isolation rooms.
SPINAL CORD INJURY/DISORDERS CENTER Acute Care Unit Patient Area and Long Term Care Unit Patient Area | BRAR1 | Isolation Anteroom | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (S) | 35 | (-) | No | CV |  | Note 1 - Special Exhaust System . Provide a dedicated, special exhaust system for the Patient Bedroom, Ante Room and Patient Toilet (where present). Do not connect other rooms to the dedicated exhaust system. Locate the exhaust fan at the end of the duct run to maintain the ductwork within the building at a negative pressure and install bag-in-bag out HEPA filters just prior to the fan inlet. Discharge exhaust air above the highest roof level through a stack at least 10 ft [3 m] tall at 3,500 fpm [18 m/s] discharge velocity. The discharge air outlet shall be located at least 25 ft [8 m] from outdoor air intakes and operable windows. Follow the recommendations of the dispersion analysis for higher than minimum requirements. Provide emergency power for the exhaust fan and associated controls. Label ductwork, filter, and fan "COMMUNICABLE DISEASE CONTAMINATED AIR". | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 - Air Distribution Layout. (a) Patient Bedroom. Locate the exhaust air inlet over or near the patient bed to ensure that air flows into the room and away from the patient room door. Preferred location of the exhaust air inlet is in the wall, 7 in [175 mm] above the floor, and near the patient head rest. (b) Ante Room. Air shall transfer from the Corridor into the Ante Room and then to the Isolation Room. The Ante Room is positive with respect to the Isolation Room and negative with respect to the Corridor. | Note 4 -Toilet Room Total Air Changes Per Hour & Negative Air Balance. Unlike other patient room / patient bathroom combinations these bathrooms will only get part of the makeup air from the patient bathroom. Each bathroom shall have its own constant volume temperature control terminal which shall provide enough makeup air to keep the bathroom a minimum of 30% negative relative to the patient room. | Note 5 - Additional Information. See room data sheets (RDS) for isolation rooms.
SPINAL CORD INJURY/DISORDERS CENTER Acute Care Unit Patient Area and Long Term Care Unit Patient Area | TSPS1 | Isolation Patient Bathroom | 75 | 24 | 70 | 21 | NA | NA | 15 | NA | Exhaust (S) | 40 | (--) | Yes | CV |  | Note 1 - Special Exhaust System . Provide a dedicated, special exhaust system for the Patient Bedroom, Ante Room and Patient Toilet (where present). Do not connect other rooms to the dedicated exhaust system. Locate the exhaust fan at the end of the duct run to maintain the ductwork within the building at a negative pressure and install bag-in-bag out HEPA filters just prior to the fan inlet. Discharge exhaust air above the highest roof level through a stack at least 10 ft [3 m] tall at 3,500 fpm [18 m/s] discharge velocity. The discharge air outlet shall be located at least 25 ft [8 m] from outdoor air intakes and operable windows. Follow the recommendations of the dispersion analysis for higher than minimum requirements. Provide emergency power for the exhaust fan and associated controls. Label ductwork, filter, and fan "COMMUNICABLE DISEASE CONTAMINATED AIR". | Note 2 - Instrumentation. Provide a room differential pressure monitoring device between Ante Room and Isolation Room, and between Ante Room and corridor. | Note 3 -Toilet Room Total Air Changes Per Hour & Negative Air Balance. Unlike other patient room / patient bathroom combinations these bathrooms will only get part of the makeup air from the patient bathroom. Each bathroom shall have its own constant volume temperature control terminal which shall provide enough makeup air to keep the bathroom a minimum of 30% negative relative to the patient room. | Note 4 - Additional Information. See room data sheets (RDS) for isolation rooms.
SPINAL CORD INJURY/DISORDERS CENTER Acute Care Unit Patient Area and Long Term Care Unit Patient Area | DAYR1 | Day Room/Lounge | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Smoking. Provide a dedicated 100% exhaust system if smoking is permitted in the lounge.
SPINAL CORD INJURY/DISORDERS CENTER Acute Care Unit Patient Area and Long Term Care Unit Patient Area | NCWD1 | Nourishment Kitchen | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G/S) | 40 | (-) | Yes | VAV |  | Note 1 - Exhaust System. Connect exhaust to a common general exhaust system. Provide 100% transfer air for the exhaust from the adjoining space. Coordinate with equipment to be used - if conditions warrant it provide NFPA 96 kitchen hood exhaust system.
SPINAL CORD INJURY/DISORDERS CENTER Acute Care Unit Patient Area and Long Term Care Unit Patient Area | LAUN1 | Patient Laundry | NA | NA | NA | NA | NA | NA | 4 | 2 | Exhaust (S) | 40 | (-) | No | VAV |  | Note 1 - Exhaust System. Provide Dryer Exhaust System. Coordinate with equipment to be used.
SPINAL CORD INJURY/DISORDERS CENTER Acute Care Unit Patient Area and Long Term Care Unit Patient Area | OFDC2 | Quiet Room | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Patient Area | DAYR1 | Multipurpose Room | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. Where the room is equipped with folding partitions, provide individual air supply, air return, and room temperature control on either side of the partition. | Note 2 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensor to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirement in ASHRAE Standard 62.1 - 2016 or latest approved edition.
SPINAL CORD INJURY/DISORDERS CENTER Patient Area | XXYYC | Internet Cafe | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Patient Area | RAMR1 | Meditation Room | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (+) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Patient Area | OFD03 | Patient Education | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Patient Area | FSCD1 | Resident Dining/Serving | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 40 | (-) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Patient Area | BTSCI | Tub Room | 78 | 26 | 82 | 28 | NA | NA | 10 | NA | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Exhaust System. Provide a dedicated or a common wet exhaust system with welded stainless steel ductwork.
SPINAL CORD INJURY/DISORDERS CENTER Patient Area | TRGM1 | Exam/Treatment Room | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Patient Area | PTWT1 | Hydrotherapy | 78 | 26 | 82 | 28 | NA | NA | 10 | NA | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Exhaust System. Provide a dedicated or a common wet exhaust system with welded stainless steel ductwork.
SPINAL CORD INJURY/DISORDERS CENTER Patient Clinic Area | TRGS1 | Exam/Treatment Room | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Note 1 | VAV |  | Note 1 - Temperature Controls. If one room is provided provide it with temperature control. If more than one room is provided follow Chapter 2 requirements.
SPINAL CORD INJURY/DISORDERS CENTER Patient Clinic Area - Urodynamics | EXUD1 | Exam/Treatment Room | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Patient Clinic Area - Urodynamics | XDCY1 | Cystoscopy | 66 | 19 | 66 | 19 | 60 | 30 | 15 | 3 | Return | 35 | (+) | Yes | VAV |  | Note 1 - Unoccupied Mode. Provide a two-position air terminal unit to deliver 50% supply air during unoccupied mode while maintaining positive air balance. | Note 2 - Air Distribution. Provide unidirectional air distribution with overhead supply and floor level return. Locate return air registers at opposite ends at 8 in [200 mm] above the floor. | Note 3 - Instrumentation. Provide temperature and relative humidity sensors for trending of indoor design conditions.
SPINAL CORD INJURY/DISORDERS CENTER Patient Clinic Area - Urodynamics | SRS01 | Instrument Cleaning Room / Storage | 66 | 19 | 72 | 22 | 55 | 30 | 10 | 10 | Exhaust (G) | 40 | (- -) | Yes | CV |  | Note 1 - Exhaust System. Connect the room exhaust to a dedicated or a common general exhaust system and transfer air from the Storage Room and Corridor.
SPINAL CORD INJURY/DISORDERS CENTER Patient Clinic Area - Urodynamics | RRSS1 | Recovery Room | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Patient Clinic Area - Urodynamics | DR001 | Dressing Room/Cubicle | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Patient Clinic Area - Urodynamics | NSTA1 | Nurse Station | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Patient Clinic Area - Urodynamics | OFD01 | Urologist Office | 72 | 22 | 82 | 28 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Note 1 | VAV |  | Note 1 - Temperature Controls. If one room is provided provide it with temperature control. If more than one room is provided follow Chapter 2 requirements.
SPINAL CORD INJURY/DISORDERS CENTER Patient Clinic Area - Urodynamics | UCCL1 | Outpatient Urodynamics Clinic Clean Utility Room | 70 | 21 | 70 | 21 | 55 | 30 | 4 | 4 | Return | 40 | (+) | Yes | CV
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | PTES1 | Physical Therapy / Kinesiology Therapy | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | OTEV1 | Occupational Therapy | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | XXYYC | PT / OT /KT Occupational Therapy | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | OTDL1 | Activities of Daily Living | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | XXYYC | Home Environment Learning Bathroom | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (-) | No | CV
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | XXYYC | Home Environment Learning Bedroom | 72 | 22 | 82 | 28 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Bedroom can be served by a common terminal unit if the rooms are located on the same exposure as shown in the SCI Design Guide dated June 2008 with 2011 Revision.
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | XXYYC | Home Environment Learning Kitchen | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (-) | No | CV |  | Note 1 - Kitchen. Exhaust room air outdoors if the kitchen equipment or room exhaust has an outdoor air connection.
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | XXYYC | Home Environment Learning Living/Dining | 72 | 22 | 82 | 28 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Living/Dining can be served by a common terminal unit if the rooms are located on the same exposure as shown in the SCI Design Guide dated June 2008 with 2011 Revision.
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | XXYYC | Horticulture Therapy | 72 | 22 | 82 | 28 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | PTWT1 | Therapeutic Pool | 80 | 27 | 85 | 29 | 65 | NA | 10 | NA | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Energy Considerations. Provide system with air flow setback capability for operation during un-occupied periods. | Note 2 - Exhaust System. Provide 100% exhaust with a dedicated or a common wet exhaust system with welded stainless steel ductwork. Evaluate the pool water evaporation load and adjust air flows to maintain space relative humidity below 65%. | Note 3 - Air Distribution. Direct supply air towards surfaces prone to condensation and located exhaust grills so as not to promote short circuiting of supply.
SPINAL CORD INJURY/DISORDERS CENTER Therapy Rooms | DR001 | Therapeutic Pool Dressing Room (One male, one female) | 78 | 26 | 82 | 28 | NA | NA | 6 | 2 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Air Balance. Transfer air from the adjoining spaces to maintain negative air balance.
SPINAL CORD INJURY/DISORDERS CENTER Support Spaces | SRLW1 | Litter Storage | 78 | 26 | 70 | 21 | NA | NA | 6 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Exhaust System. Transfer air from the adjoining spaces to maintain negative air balance. | Note 2 - Room Temperature Control. Individual room temperature control is optional. The room can be served by a common air terminal unit with similar load characteristics.
SPINAL CORD INJURY/DISORDERS CENTER Support Spaces | SRE01 | Transfer Equipment Storage | 78 | 26 | 70 | 21 | NA | NA | 4 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Exhaust System. Connect exhaust to a general exhaust system serving other spaces. Transfer air from the adjoining spaces to maintain negative air balance. | Note 2 - Room Temperature Control. Individual room temperature control is optional. The room can be served by a common air terminal unit with similar load characteristics.
SPINAL CORD INJURY/DISORDERS CENTER Support Spaces | TLTS1 | Patient (Litter) Bathroom | 75 | 24 | 70 | 21 | NA | NA | 15 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Exhaust System and Temperature Control. Unlike other patient bathroom these bathrooms will only get part of the makeup air from the exterior space. Each bathroom shall have its own constant volume temperature control terminal which shall provide enough makeup air to keep the bathroom a minimum of 30% negative relative to the patient room.
STERILE PROCESSING SERVICE | [16 empty] | Note 1 - General: The rooms and their relative locations with adjoining spaces are based on information given in the VA Sterile Processing Service Design Guide dated October 1, 2015; VHA Directive 1116 Dated March 23, 2016 and in the VA PG-18-9 Space Planning Criteria Chapter 285 dated March 2008 and revised October 3, 2016. The design documents must include a space pressure and air flow diagram to indicate all required pressure relationships. Provide room differential pressure monitoring devices for the following spaces: Decontamination area , Packaging & Preparation area, Clean Workroom & Storage area, Anteroom and Dispatch areas. These devices must be provided at all openings in common walls between these areas and adjacent spaces.
STERILE PROCESSING SERVICE Decontamination Area | CSCR1 | Soiled Transition / Drop Off Ante Room | 66 | 19 | 72 | 22 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (-) | Yes | CV
STERILE PROCESSING SERVICE Decontamination Area | CSPE1 | PPE Alcove | 66 | 19 | 72 | 22 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (+) | Yes | CV
STERILE PROCESSING SERVICE Decontamination Area | CSDE1 | Decontamination Work Area | 66 | 19 | 72 | 22 | 60 | 30 | 6 | 6 | Exhaust (G) | 40 | (--) | Yes | CV
STERILE PROCESSING SERVICE Decontamination Area | CWSH2 | Automatic Cart Washer | NA | NA | NA | NA | NA | NA | Note 1 | Note 1 | Exhaust (S) | 45 | (-) | No | CV |  | Note 1 - Special Exhaust System. Coordinate exhaust and makeup air from automatic cart washer with the basis of design cart washer system. Provide with welded stainless steel wet exhaust system.
STERILE PROCESSING SERVICE Decontamination Area | CWSH3 | Manual Cart Wash | 75 | 24 | 70 | 21 | NA | NA | 10 | 10 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Air Terminal Unit. Provide a cooling only dedicated air terminal unit to serve the Manual Equipment Wash room. Specify this unit as stainless steel construction with copper fins on copper tube chilled water coil. | Note 2 - Special Exhaust Systems. Provide a dedicated wet exhaust system to serve this space and the Automatic Cart Washer room.
STERILE PROCESSING SERVICE Decontamination Area | CSWT1 | Water Treatment and Detergent Storage Room | NA | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (G) | 40 | (-) | No | CV |  | Note 1 - Individual Room Temperature Control. Individual room temperature control of 72 F (22 C) cooling and heating with supply air is required if the space is occupied.
STERILE PROCESSING SERVICE Decontamination Area | JANC2 | Housekeeping Aides Closet (HAC) | 75 | 24 | 75 | 24 | NA | NA | 10 | 10 | Exhaust (G) | 40 | (- -) | No | CV
STERILE PROCESSING SERVICE Scope Processing Area | CSAR1 | Scope Processing Anteroom | 66 | 19 | 72 | 22 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Provide supply air from an adjoining air terminal unit, as individual room temperature control is not required. Direct air flow towards interior doors. Do not exhaust air from this room.
STERILE PROCESSING SERVICE Scope Processing Area | CSPE1 | PPE Alcove | 66 | 19 | 72 | 22 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (+) | Yes | CV
STERILE PROCESSING SERVICE Scope Processing Area | CSSD1 | Decontamination Room | 66 | 19 | 72 | 22 | 60 | 30 | 6 | 6 | Exhaust (G) | 40 | (--) | Yes | CV
STERILE PROCESSING SERVICE Scope Processing Area | CSSP1 | Scope Processing Room | 66 | 19 | 72 | 22 | 60 | 30 | 6 | 6 | Exhaust (G) | 40 | (-) | Yes | CV
STERILE PROCESSING SERVICE Scope Processing Area | CSST1 | Scope Staging Room | 66 | 19 | 72 | 22 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (+) | Yes | CV
STERILE PROCESSING SERVICE Preparation and Assembly Area | CSIA1 | Clean Workroom Instrument Set Assembly | 66 | 19 | 72 | 22 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (+ +) | Yes | CV
STERILE PROCESSING SERVICE Preparation and Assembly Area | SRSP1 | Sterile Processing Supplies Storage | 66 | 19 | 75 | 24 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (+) | Yes | CV
STERILE PROCESSING SERVICE Sterilization Area | CSSS1 | Steam Sterilization Area | 66 | 19 | 75 | 24 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (+ +) | Yes | CV
STERILE PROCESSING SERVICE Sterilization Area | CSSS1 | Sterilizer Equipment Room | 85 | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (G) | 45 | (-) | No | CV |  | Note 1 - General. Coordinate the canopy hood (generally provided for the capture of vapor) design with the architectural and equipment drawings.
STERILE PROCESSING SERVICE Sterilization Area | CSLT1 | Low Temp Sterilization Area | 66 | 19 | 75 | 24 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (+ +) | Yes | CV
STERILE PROCESSING SERVICE Sterilization Area | CSE01 | ETO Sterilizer Room | 66 | 19 | 75 | 24 | 60 | 30 | 10 | 10 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - General. Provide a dedicated exhaust system to serve the ETO Sterilizer Room and abator. See AHU System Data Sheet for details. In most cases the abator will be located in the ETO sterilizer room. | Note 2 - Flammable Storage Cabinet. Provide exhaust ventilation through the flammable storage cabinet. The cabinet exhaust shall be connected to the ETO exhaust system. Ensure compliance with NFPA 30 and applicable OSHA Regulations. | Note 3 - Alarms and Controls. Provide an alarm panel outside the ETO Sterilizer Room to sound a local alarm and remote alarm at the ECC in the event of loss or interruption of exhaust airflow. Integrate ETO gas leakage alarm with the exhaust system alarm.
STERILE PROCESSING SERVICE Sterilization Area | CSE02 | ETO Abator Room | 66 | 19 | 75 | 24 | 60 | 30 | 10 | 10 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - General. Provide a dedicated exhaust system to serve the ETO Sterilizer Room and abator. See AHU System Data Sheet for details. In most cases the abator will be located in the ETO sterilizer room. | Note 2 - Flammable Storage Cabinet. Provide exhaust ventilation through the flammable storage cabinet. The cabinet exhaust shall be connected to the ETO exhaust system. Ensure compliance with NFPA 30 and applicable OSHA Regulations. | Note 3 - Alarms and Controls. Provide an alarm panel outside the ETO Sterilizer Room to sound a local alarm and remote alarm at the ECC in the event of loss or interruption of exhaust airflow. Integrate ETO gas leakage alarm with the exhaust system alarm.
STERILE PROCESSING SERVICE Sterilization Area | CHC01 | Cart Return Area | 66 | 19 | 75 | 24 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (+ +) | Yes | CV
STERILE PROCESSING SERVICE Sterilization Area | CHC01 | Unloading / Cooling Area | 66 | 19 | 75 | 24 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (+ +) | Yes | CV |  | Note 1 - General. These areas at the sterilizer unloading area are part of the larger room. Provide exhaust grills and / or exhaust hoods at the sterilizer loading and unloading ends to capture heat and moisture as directly as possible.
STERILE PROCESSING SERVICE Sterilization Area | CSCG1 | Clean Steam Generator Equipment | 85 | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (G) | 45 | (-) | No | CV |  | Note 1 - General. Coordinate the canopy hood (generally provided for the capture of vapor) design with the architectural and equipment drawings.
STERILE PROCESSING SERVICE Receiving, Storage and Dispatch Area | SRS01 | Vendor Drop-Off / Pick-up Area | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 6 | Exhaust (G) | 40 | (+) | Yes | CV
STERILE PROCESSING SERVICE Receiving, Storage and Dispatch Area | CHC01 | Dispatch Area | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (o) | Yes | CV
STERILE PROCESSING SERVICE Receiving, Storage and Dispatch Area | OFA07 | Case Cart Dispatch Workstation | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (+) | Yes | CV
STERILE PROCESSING SERVICE Receiving, Storage and Dispatch Area | SRS05 | Sterile Durables (RMEs) Storage | 66 | 19 | 72 | 22 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (+) | Yes | CV
STERILE PROCESSING SERVICE Receiving, Storage and Dispatch Area | CSCQ1 | Case Cart Assembly Area | 66 | 19 | 75 | 24 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (+) | Yes | CV
STERILE PROCESSING SERVICE Receiving, Storage and Dispatch Area | SRS04 | Sterile Consumables (Soft Goods) Storage | 66 | 19 | 72 | 22 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (+) | Yes | CV |  | Note 1- Temperature and Humidity Control. Depending on the size and location of the satellite storage it may or may not be possible to achieve the listed temperature and relative humidity conditions. This will depend on the proximity of an air handling unit with the adequate level of dehumidification and humidification. | Note 2- Filtration. Even if temperature and humidity requirements cannot be met, ensure filtration levels meet or exceed the SPS air handling unit requirements. | Note 3 - Pressure Control. Due to the small size of satellite storage areas 4 air changes per hour may not be adequate to provide a measurable pressure drop in the room. The designer shall analyze the room characteristics and increase design air flow as necessary to maintain 0.02 inch water column between the room and the adjoining corridors.
STERILE PROCESSING SERVICE Receiving, Storage and Dispatch Area | JANC2 | Housekeeping Aides Closet (HAC) | NA | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (G) | 40 | (- -) | No | CV
STERILE PROCESSING SERVICE Staff and Administrative Area | OFA09 | Sterile Processing Service (SPS) Chief Office | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 4 | Exhaust (G) | 35 | (o) | Yes | VAV
STERILE PROCESSING SERVICE Staff and Administrative Area | OFA09 | Sterile Processing Service (SPS) Assistant Chief Office | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 4 | Exhaust (G) | 35 | (o) | Yes | VAV
STERILE PROCESSING SERVICE Staff and Administrative Area | OFA07 | Clerical Workstation | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (o) | No | VAV |  | Note 1 - Room Air Balance. Provide supply air from an adjoining air terminal unit.
STERILE PROCESSING SERVICE Staff and Administrative Area | CFR01 | Staff Training Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 6 | Exhaust (G) | 35 | (o) | Yes | VAV
STERILE PROCESSING SERVICE Staff and Administrative Area | RPR01 | Copier / Office Supply Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (o) | No | VAV |  | Note 1 - Room Air Balance. Provide supply air from an adjoining air terminal unit.
STERILE PROCESSING SERVICE Staff and Administrative Area | SL001 | Staff Lounge | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 4 | Exhaust (G) | 35 | (o) | Yes | VAV |  | Note 1 - Exhaust. Exhaust if food preparation odors are expected. Otherwise return.
STERILE PROCESSING SERVICE Staff and Administrative Area | TNPG1 | Staff Toilet (male and female) | NA | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (G) | 40 | (--) | No | CV
STERILE PROCESSING SERVICE Staff and Administrative Area | LR002 | Male Locker / Changing Room | 75 | 24 | 70 | 21 | NA | NA | 6 | 6 | Exhaust (G) | 40 | (-) | No | CV |  | Note 1- Room Air Balance. Maintain locker rooms under negative air balance with respect to PPE and positive air balance with respect to the connecting Clean Toilet/Showers - Women.
STERILE PROCESSING SERVICE Staff and Administrative Area | LR002 | Female Locker / Changing Room | 75 | 24 | 70 | 21 | NA | NA | 6 | 6 | Exhaust (G) | 40 | (-) | No | CV |  | Note 1- Room Air Balance. Maintain locker rooms under negative air balance with respect to PPE and positive air balance with respect to the connecting Clean Toilet/Showers - Women.
STERILE PROCESSING SERVICE Staff and Administrative Area | TSSU1 | Male Toilet / Shower | NA | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (G) | 40 | (--) | No | CV
STERILE PROCESSING SERVICE Staff and Administrative Area | TSSU1 | Female Toilet / Shower | NA | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (G) | 40 | (--) | No | CV
SURGICAL SUITE | [16 empty] | Note 1 - General: The rooms and their relative locations with adjoining spaces are based on information given in the VA Design Guide for the Surgical Service dated April 2016.
SURGICAL SUITE General: The rooms and their relative locations with adjoining spaces are based on information given in the VA Design Guide for the Surgical Service dated April 2016. | RRPR1 | Pre-Operative Holding / Phase II Recovery Patient Bay | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+) | Yes | CV | 6 | Note 1 - Size reheat coils to allow space heating to 86F / 30 C in demand.
SURGICAL SUITE | RRPR2 | Pre-Operative Holding / Phase II Recovery Patient Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+) | Yes | CV | 6 | Note 1 - Size reheat coils to allow space heating to 86F / 30 C in demand.
SURGICAL SUITE | ANCW2 | Anesthesia Clean Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | CV | 6
SURGICAL SUITE Operating Rooms. | ORGS1 | General Operating Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation.
SURGICAL SUITE Operating Rooms. | OROS1 | Orthopedic Operating Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation.
SURGICAL SUITE Operating Rooms. | ORCS1 | Urology / Cystoscopy Operating Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation.
SURGICAL SUITE Operating Rooms. | ORCT1 | Cardiothoracic Operating Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation.
SURGICAL SUITE Operating Rooms. | ORHL1 | Cardiothoracic / Hybrid OR Pump Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation.
SURGICAL SUITE Operating Rooms. | ORNS1 | Neurosurgical Operating Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation.
SURGICAL SUITE Operating Rooms. | ORRB1 | Robotics Operating Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation.
SURGICAL SUITE Operating Rooms. | ORTR1 | Transplant Operating Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation.
SURGICAL SUITE Operating Rooms. | ORHY1 | Monoplane Hybrid Operating Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation. | Note 2 - Diffusers. Use only laminar flow diffusers in this room. | Note 3 - Sterile Field. Carefully design large sterile field to keep velocity low enough to preclude the possibility of turbulent flow over the imaging equipment gantry. Mechanical engineer is responsible for maintaining sterile flow aseptic field and minimizing turbulence.
SURGICAL SUITE Operating Rooms. | ORHY2 | Biplane Hybrid Operating Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation. | Note 2 - Diffusers. Use only laminar flow diffusers in this room. | Note 3 - Sterile Field. Carefully design large sterile field to keep velocity low enough to preclude the possibility of turbulent flow over the imaging equipment gantry. Mechanical engineer is responsible for maintaining sterile flow aseptic field and minimizing turbulence.
SURGICAL SUITE Operating Rooms. | ORHC1 | Hybrid OR Control Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 40 | (o) | Yes | VAV | 4
SURGICAL SUITE | XCCE1 | Cardiac Catheterization Laboratory | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation. | Note 2 - Diffusers. Use only laminar flow diffusers in this room. | Note 3 - Sterile Field. Carefully design large sterile field to keep velocity low enough to preclude the possibility of turbulent flow over the imaging equipment gantry. Mechanical engineer is responsible for maintaining sterile flow aseptic field and minimizing turbulence.
SURGICAL SUITE | XCEP1 | Electrophysiology Procedure Room | 66 | 19 | 75 | 24 | 60 | 30 | 20 | 4 | Return | 40 | (++) | Yes | CV | 10 | Note 1 - Air Balance. Positive with respect to clean core during occupied and unoccupied modes of operation. | Note 2 - Diffusers. Use only laminar flow diffusers in this room. | Note 3 - Sterile Field. Carefully design large sterile field to keep velocity low enough to preclude the possibility of turbulent flow over the imaging equipment gantry. Mechanical engineer is responsible for maintaining sterile flow aseptic field and minimizing turbulence.
SURGICAL SUITE | TRTE1 | Transesophageal Echocardiograph (TEE) Procedure Room | 75 | 24 | 70 | 21 | 60 | 30 | 10 | 2 | Return | 35 | (-) | Yes | CV | 10
SURGICAL SUITE | TRTE2 | TEE Probe Decontamination Room | 69 | 20 | 69 | 20 | 55 | 30 | 10 | 10 | Exhaust (G) | 40 | (--) | Yes | CV | 10 | Note 1 - Air Balance. Negative to Semi-Restricted Corridor during occupied and unoccupied modes of operation.
SURGICAL SUITE | TRTE3 | Clean TEE Probe Storage | 70 | 21 | 70 | 21 | 55 | 30 | 4 | 2 | Return | 35 | (o) | Yes | CV | 4
SURGICAL SUITE | ORSR1 | Immediate Use Sterilization Room | 69 | 20 | 69 | 20 | 60 | 30 | 10 | 2 | Exhaust (G) | 40 | (- -) | Yes | CV | 10 | Note 1 - Room Exhaust. Transfer room air to the Sterilizer Equipment Room and connect to the general exhaust system. This room is positive with respect to the equipment room.
SURGICAL SUITE | RRBP1 | Phase I Recovery PACU Patient Bay | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (+) | Yes | CV | 6 | Note 1 - Room Temperature Control. Size the terminal reheat coil to maintain 86 F [30 C] room temperature on demand. | Note 2 - Filtration Requirements. For PACUs not served by the Surgical Suite AHU, provide terminal HEPA filters on the downstream side of each air terminal unit otherwise use same filtration used in OR. See Surgical AHU filtration notes.
SURGICAL SUITE | RRIR1 | Airborne Infection Isolation (AII) Phase I Recovery PACU Patient Room | 75 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Exhaust (S) | 35 | (--) | Yes | CV | 6 | Note 1 - General. See Airborne Infection Isolation (AII) room data sheets for additional requirements for the AII room and the anteroom.
SURGICAL SUITE | LBUL1 | Frozen Section Laboratory | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 40 | (-) | Yes | CV | 6
SURGICAL SUITE | USCL7 | Surgical Soiled Utility Room | NA | NA | NA | NA | NA | NA | 12 | NA | Exhaust (G) | 45 | (- -) | No | CV | 12 | Note 1 - Room Exhaust. Transfer air from the adjoining spaces for exhaust.
SURGICAL SUITE | XXXXX | Clean Core | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 40 | (+) | Yes | VAV | 4 | Note 1 - Air Balance. Negative with respect to the Operating and Cystoscopy Rooms during occupied and unoccupied modes of operation.
SURGICAL SUITE | XXXXX | Gas Cylinder Storage Room | NA | NA | NA | NA | NA | NA | 6 | NA | Exhaust (G) | 40 | (- -) | No | CV | 6 | Note 1 - Room Exhaust. Transfer air from adjoining spaces for exhaust. Do not supply air under positive air pressure.
SURGICAL SUITE | XXXXX | Heart Lung Machine Preparation | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV | 3
SURGICAL SUITE | XXXXX | Nerve Block Induction Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (+) | Yes | VAV | 5 | Note 1 - Room Air Balance. Positive during occupied and unoccupied modes of operation.
SURGICAL SUITE | XXXXX | Plaster Splint Storage | NA | NA | NA | NA | NA | NA | 6 | NA | Exhaust (G) | 40 | (-) | No | CV | 6
SURGICAL SUITE | XXXXX | Radiographic Film Processing Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Exhaust (G) | 40 | (-) | Yes | CV | 8 | Note 1 - Room Air Return. Return air is not permitted if chemicals are used in film processing.
SURGICAL SUITE | XXXXX | Semi-Restricted Corridor | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Return | 40 | (o) | Yes | VAV | 4 | Note 1 - Room Air Balance. Maintain negative air balance with respect to the Operating and Cystoscopy Rooms and positive to other adjoining spaces.
SURGICAL SUITE | XXXXX | Sub-Sterile Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 40 | (- -) | Yes | CV | 6 | Note 1 - Room Exhaust. Transfer room air to the Sterilizer Equipment Room and connect to the general exhaust system. This room is positive with respect to the equipment room.
Veterinary Medical Unit (VMU) | SB173 | VMU Female Staff Shower, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Veterinary Medical Unit (VMU) | SB184 | VMU Male Staff Shower, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Veterinary Medical Unit (VMU) | SB202 | VMU Female Staff Toilet, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Veterinary Medical Unit (VMU) | SB203 | VMU Male Staff Toilet, Bldg Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Veterinary Medical Unit (VMU) | SB244 | VMU Housekeeping Aides Closet (HAC), Bldg Sprt | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV
Veterinary Medical Unit (VMU) | SB522 | VMU Breakdown Room, Lgstcs Svc | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Veterinary Medical Unit (VMU) | SB531 | VMU Staging Room, Lgstcs Svc | 79 | 26 | 68 | 20 | 70 | 30 | 15 | 15 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Heating System. Provide an air curtain with a heating element. Interlock the air curtain start with the loading dock door operating mechanism. Activate heating when the ambient temperature drops below 45 F [7 C] temperature.
Veterinary Medical Unit (VMU) | SB684 | VMU Loading Dock, Lgstcs Svc | NA | NA | 60 | 15 | NA | NA | NA | NA | Return | 45 | (o) | Yes | CV |  | Note 1 - Heating System. Provide an air curtain with a heating element. Interlock the air curtain start with the loading dock door operating mechanism. Activate heating when the ambient temperature drops below 45 F [7 C] temperature.
Veterinary Medical Unit (VMU) | SC741 | VMU General Procedure / Treatment Room, R&D | 72 | 22 | 72 | 22 | 55 | 40 | 8 | 8 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Exhaust Air. Pick-Up. Collect room exhaust air at approximately 7 in [175 mm] above the floor level through 1 in [25 mm] thick, MERV 6 filter grille.
Veterinary Medical Unit (VMU) | SC747 | VMU Irradiator Room, R&D | 72 | 22 | 72 | 22 | 55 | 40 | 15 | 15 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Fume Hood Exhaust. Provide a dedicated exhaust system for the fume hood.
Veterinary Medical Unit (VMU) | SC748 | VMU Diagnostic Laboratory, R&D | 72 | 22 | 72 | 22 | 55 | 40 | 15 | 15 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Exhaust. Coordinate exhaust with equipment, such as, fume hoods and/or Biological Safety Cabinets.
Veterinary Medical Unit (VMU) | SC751 | VMU Surgical Preparation Room, R&D | 65 | 18 | 65 | 18 | 60 | 45 | 4 | 4 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Room Air Balance. While maintaining negative air balance with respect to the adjoining operating rooms, adjust exhaust air volume as required.
Veterinary Medical Unit (VMU) | SC752 | VMU Operating Room (OR), R&D | 65 | 18 | 65 | 18 | 60 | 45 | 15 | 15 | Exhaust (G) | 35 | (+) | Yes | CV
Veterinary Medical Unit (VMU) | SC753 | VMU Recovery Room, R&D | 65 | 18 | 80 | 27 | 60 | 45 | 10 | 10 | Exhaust (G) | 40 | (+ +) | Yes | CV |  | Note 1 - Room Temperature Adjustment. Size the reheat coil to maintain higher space temperature on demand.
Veterinary Medical Unit (VMU) | SC754 | VMU Gown / Scrub Room, R&D | 72 | 22 | 72 | 22 | 60 | 45 | 4 | 4 | Exhaust (G) | 35 | (+) | Yes | CV
Veterinary Medical Unit (VMU) | SC755 | VMU Workroom, R&D | 72 | 22 | 72 | 22 | 60 | 45 | 4 | 4 | Exhaust (G) | 35 | (o) | Yes | CV |  | Note 1 - Room Exhaust. Draw exhaust air over the sterilizer hood. Adjust supply air volume to meet the exhaust needs.
Veterinary Medical Unit (VMU) | SC756 | VMU Surgical Supply Storage Room, R&D | 72 | 22 | 72 | 22 | 60 | 45 | 4 | 4 | Exhaust (G) | 35 | (o) | Yes | CV |  | Note 1 - Room Exhaust. Draw exhaust air over the sterilizer hood. Adjust supply air volume to meet the exhaust needs.
Veterinary Medical Unit (VMU) | SC761 | VMU Imaging / Behavioral Study Preparation Room, R&D | 72 | 22 | 72 | 22 | 60 | 45 | 8 | 8 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Temperature. Adjust temperature setpoint to match the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC762 | VMU Imaging / Behavioral Study Animal Holding Room, R&D | 72 | 22 | 72 | 22 | 60 | 45 | 8 | 8 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Temperature. Adjust temperature setpoint to match the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC763 | VMU Behavioral Study Room, R&D | 79 | 26 | 68 | 20 | 70 | 30 | 15 | 15 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Exhaust Air Pick-Up. Provide exhaust air inlets at base corners and center the ceiling supply outlet in each cubical to ensure uniform air distribution. | Note 2 - Room Temperature. Adjust temperature setpoint within the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC764 | VMU Imaging Study Room, R&D | 79 | 26 | 68 | 20 | 70 | 30 | 15 | 15 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Exhaust Air Pick-Up. Provide exhaust air inlets at base corners and center the ceiling supply outlet in each cubical to ensure uniform air distribution. | Note 2 - Room Temperature. Adjust temperature setpoint within the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC771 | VMU Small Animal Holding Room, R&D | 79 | 26 | 68 | 20 | 70 | 30 | 15 | 15 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Exhaust Air Pick-Up. Provide exhaust air inlets at base corners and center the ceiling supply outlet in each cubical to ensure uniform air distribution. | Note 2 - Room Temperature. Adjust temperature setpoint within the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC772 | VMU Behavioral / Metabolic Studies Small Animal Holding Room, R&D | 79 | 26 | 68 | 20 | 70 | 30 | 15 | 15 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Exhaust Air Pick-Up. Provide exhaust air inlets at base corners and center the ceiling supply outlet in each cubical to ensure uniform air distribution. | Note 2 - Room Temperature. Adjust temperature setpoint within the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC773 | VMU BSL-2 Small Animal Holding Room, R&D | 79 | 26 | 68 | 20 | 70 | 30 | 15 | 15 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Exhaust Air Pick-Up. Provide exhaust air inlets at base corners and center the ceiling supply outlet in each cubical to ensure uniform air distribution. | Note 2 - Room Temperature. Adjust temperature setpoint within the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC774 | VMU BSL-2 Small Animal Anteroom, R&D | 79 | 26 | 68 | 20 | 70 | 30 | 15 | 15 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Room Temperature. Adjust temperature setpoint to match the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC775 | VMU Large Animal Holding Room, R&D | 84 | 29 | 61 | 16 | 70 | 45 | 15 | 15 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Exhaust Air. Pick-Up. Provide exhaust air inlets at base corners and center the ceiling supply outlet in each cubical to ensure uniform air distribution. | Note 2 - Room Temperature. Adjust temperature setpoint to match the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC778 | VMU Small Animal Quarantine Holding Room, R&D | 72 | 22 | 72 | 22 | 55 | 45 | 15 | 15 | Exhaust (S) | 35 | (--) | Yes | CV |  | Note 1 - Room Air Distribution. Coordinate supply and exhaust air distribution with the Quarantine Room layout. Provide multiple exhaust air grilles over each quarantine area. | Note 2 - Room Temperature. Adjust temperature setpoint to match the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC779 | VMU Large Animal Quarantine Holding Room, R&D | 72 | 22 | 72 | 22 | 55 | 45 | 15 | 15 | Exhaust (S) | 35 | (--) | Yes | CV |  | Note 1 - Room Air Distribution. Coordinate supply and exhaust air distribution with the Quarantine Room layout. Provide multiple exhaust air grilles over each quarantine area. | Note 2 - Room Temperature. Adjust temperature setpoint to match the range appropriate for the animal species being studied. Refer to AAALAC - Guide for the Care and Use of Laboratory Animals.
Veterinary Medical Unit (VMU) | SC781 | VMU Necropsy Room, R&D | 72 | 22 | 72 | 22 | 55 | 40 | 15 | 15 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Exhaust Coordination. Coordinate exhaust over the trimming and necropsy tables.
Veterinary Medical Unit (VMU) | SC791 | VMU Soiled Cage Room, R&D | 72 | 22 | 72 | 22 | 55 | 40 | 20 | 20 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Wet Exhaust. System. Provide a dedicated wet exhaust system to serve the Cage Washer Room and Cage Wash Room (with Tunnel Washer Room).
Veterinary Medical Unit (VMU) | SC792 | VMU Cagewash Equipment Room, R&D | 77 | 25 | 77 | 25 | 55 | 40 | 15 | 15 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Wet Exhaust. System. Provide a dedicated wet exhaust system to serve the Cage Washer Room and Cage Wash Room (with Tunnel Washer Room).
Veterinary Medical Unit (VMU) | SC793 | VMU Clean Cage Room, R&D | 77 | 25 | 70 | 21 | 55 | 40 | 6 | 6 | Exhaust (G) | 40 | (+) | Yes | CV |  | Note 1 - Wet Exhaust. System. Provide a dedicated wet exhaust system to serve the Cage Washer Room and Cage Wash Room (with Tunnel Washer Room).
Veterinary Medical Unit (VMU) | SC794 | VMU Sterilizer Equipment Room, R&D | 77 | 25 | 77 | 25 | 55 | 40 | 15 | 15 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Wet Exhaust. System. Provide a dedicated wet exhaust system to serve the Cage Washer Room and Cage Wash Room (with Tunnel Washer Room).
Veterinary Medical Unit (VMU) | SC797 | VMU Cagewash Detergent Storage Room, R&D | 77 | 25 | 70 | 21 | 55 | 40 | 6 | 6 | Exhaust (G) | 40 | (+) | Yes | CV |  | Note 1 - Room Exhaust. Collect exhaust through the hood over the sterilizer.
Veterinary Medical Unit (VMU) | SC798 | VMU Bedding Storage Room, R&D | NA | NA | NA | NA | NA | NA | 4 | 4 | Exhaust (G) | 40 | (o) | No | CV |  | Note 1 - Room Supply. Air Provide a ducted, supply air takeoff from an adjoining air terminal unit.
Veterinary Medical Unit (VMU) | SC799 | VMU Animal Food Preparation Room, R&D | NA | NA | NA | NA | NA | NA | 4 | NA | Exhaust (G) | 45 | (--) | No | CV |  | Note 1 - Room Exhaust. Transfer air from the adjoining space for exhaust. Do not provide supply air.
Veterinary Medical Unit (VMU) | SC801 | VMU Receiving Room, R&D | 72 | 22 | 72 | 22 | 55 | 45 | 10 | 10 | Exhaust (G) | 35 | (-) | Yes | CV |  | Note 1 - Exhaust Air Pick-Up. Collect room exhaust air at approximately 7 in [175 mm] above the floor level through 1 in [25 mm] thick, MERV 6 filter grille.
Veterinary Medical Unit (VMU) | SC802 | VMU Laundry Room, R&D | 78 | 26 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G ) | 45 | (-) | Yes | CV |  | Note 1 – Soiled Receiving and Sorting Room This contaminated room is separated from the clean side by the washer / extractors and typically has a high ceiling mounted track system for trolley cars that are used to move the bags of laundry. Therefore the air supply ductwork and grills are mounted high above the tracks. The air distribution should be directional with supply slots or high wall grills blowing down at the far end away from the loading doors of the washer extractors towards the door and exhaust grills in a line directly above the washer / extractor doors.
Veterinary Medical Unit (VMU) | SC803 | VMU General Storage Room, R&D | NA | NA | NA | NA | NA | NA | 4 | NA | Return | 40 | (+) | No | CV |  | Note 1 - HVAC Treatment. (a) For a small, 100 sf [9 m2] and smaller, unoccupied room, individual room temperature control is not required. Room can be supplied from any adjoining constant- volume air terminal unit serving similar interior or perimeter space. Ducted return air pick-up is also not required, as the room air can ex-filtrate into adjoining spaces, such as, a non-exit corridor (NFPA 90A). (b) Individual room temperature control is required for a large, more than 100 sf [9 m2], occupied room. Provide a minimum of 2 ACH outdoor air.
Veterinary Medical Unit (VMU) | SC804 | VMU Carcass Freezer Room, R&D | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV |  | Note 1 - Room Exhaust. Maintain double negative air balance by drawing all transfer air from the adjoining space.
Veterinary Medical Unit (VMU) | SC805 | VMU Waste Room, R&D | NA | NA | NA | NA | NA | NA | 10 | 10 | Exhaust (S) | 40 | (- -) | No | CV |  | Note 1 - Exhaust System. Provide a dedicated exhaust system. Terminate exhaust at least 10 ft. [3 m] above the highest roof level. Discharge exhaust at 3,500 fpm [18 m/s] and/or according to the dispersion analysis recommendations. Evaluate the need for filtration in the exhaust air duct before discharging outdoors. Consult with the end users and local safety officer for exhaust air filtration requirements.
Veterinary Medical Unit (VMU) | SC806 | VMU Food Storage Room, R&D | 36 | 2.2 | 36 | 2.2 | NA | NA | NA | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Exhaust. Provide transfer air through ducted ceiling connection. Provide a dedicated refrigeration unit.
Veterinary Medical Unit (VMU) | SS204 | VMU Veterinarian Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
Veterinary Medical Unit (VMU) | SS205 | VMU Supervisor Office, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
Veterinary Medical Unit (VMU) | SS218 | VMU Veterinary Research Associate Workstation, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
Veterinary Medical Unit (VMU) | SS232 | VMU Female Staff Locker Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Veterinary Medical Unit (VMU) | SS241 | VMU Male Staff Locker Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
Veterinary Medical Unit (VMU) | SS262 | VMU Staff Breakroom, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air. Return air is permitted if the lounge is not equipped with vending machines, microwave, refrigerator, etc., otherwise follow requirements in ASHRAE Standard 62.1
Veterinary Medical Unit (VMU) | SS268 | VMU Copy / Supply Room, Stff Sprt | NA | NA | NA | NA | NA | NA | 6 | NA | Exhaust (G) | 40 | (-) | No | CV |  | Note 1 - Usage. Copy/Printing Room (Small) is a local room serving a single department only, with no more than 2 machines. | Note 2 - Conditioning. Conditioned air is drawn from other areas to ventilate the room and reduce the heat load.
Veterinary Medical Unit (VMU) | SS285 | VMU Huddle Room, Stff Sprt | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Admission | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | CV
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Barber Shop | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (-) | Yes | VAV |  | Note 1 - Exhaust Requirements. Per ASHRAE 62.1 - 2016 (or latest approved edition),, the barber shop should be exhausted at the rate of 0.5 cfm/sf [2.5 L/s/m2], while returning the remaining air, if any.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Chapel | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Dedicated Air-Handling Unit. For chapels requiring 5,000 cfm [2,360 L/s] and higher supply air volume, provide a dedicated air-handling unit to facilitate energy conservation initiatives.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Class Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2 ) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Conference Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Corridors | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | CV |  | Note 1 - Supply Air Volume. Increase the supply air volume, as required, to meet the transfer air demands of the adjoining spaces, such as, toilets, janitor closets, soiled utility rooms, laboratories, spaces requiring negative air balance, and exterior doors requiring ex-filtration.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Dressing Room | NA | NA | NA | NA | NA | NA | 4 | NA | Return | 35 | (o) | No | VAV |  | Note 1 - Room Supply. Supply air from an adjoining air terminal unit with similar load characteristics.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Gift Shop (Retail Store) | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Library | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (O) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Locker Room (with Toilets) | 75 | 24 | 70 | 21 | 60 | 30 | 10 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Transfer supply air to the toilets and showers. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Locker Room (without Toilets) | 75 | 24 | 70 | 21 | 60 | 30 | 6 | NA | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air Balance. Maintain locker rooms under negative air balance with respect to the adjoining spaces.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Lounge | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - Room Air. Return air is permitted if the lounge is not equipped with vending machines, microwave, refrigerator, etc., otherwise follow requirements in ASHRAE Standard 62.1 - 2016 or latest approved edition.
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Audio Visual Storage/Checkout | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Camera Copy | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Client Review Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 35 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Computer Imaging System Network | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Darkroom (Printing/Enlarging) | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 35 | (-) | Yes | VAV |  | Note 1 - Darkroom (Printing/Enlarging) and Photo Finishing. Exhaust room air if chemicals are used for film processing.
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Expanded Core - Illustration Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Expanded Core - Stat Camera | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Photo Finishing | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (G) | 35 | (-) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Photo Studio/Audio Visual Recording | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 30 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Photomicrography | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS Medical Media Service | XXXXX | Video Editing CCTV Control Room | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 35 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Medical Records | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Medication Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Multipurpose Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Energy Conservation Initiative. Evaluate the feasibility of using a carbon-dioxide (CO2) and/or occupancy sensors to conserve energy during part load conditions. The control sequence shall be project-specific. Follow requirements in ASHRAE Standard 62.1 - 2016 or the latest approved edition. | Note 2 - Folding Partitions. Where the room is equipped with folding partitions, provide individual room temperature control, supply diffusers and returns grills on both sides of the partition.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Offices | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV |  | Note 1 - Room Temperature Control. See Chapter 2 for individual room temperature control requirements.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Pool Dressing/Toilet/Shower - Male/Female | 75 | 24 | 70 | 21 | 60 | 30 | 4 | NA | Exhaust (G) | 45 | (-) | Yes | CV
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Toilets - Public (Interior) | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Toilets - Public (Perimeter) | NA | NA | 68 | 20 | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | Yes | CV |  | Note 1 - Perimeter Heating. For toilets with an exterior wall subject to heat loss, provide thermostatically-controlled (closed-loop, local control) terminal heater(s) to maintain set point.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Waiting Rooms | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Return | 40 | (0) | Yes | VAV |  | Note 1 - General. See below for waiting rooms in emergency department and radiology waiting rooms.
NON PATIENT ROOMS - SUPPORT AREAS | XXXXX | Waiting Rooms in Emergency Department and In Radiology | 75 | 24 | 70 | 21 | 60 | 30 | 12 | 2 | Exhaust (G) | 40 | (-) | Yes | CV |  | Note 1 - General. The 100% exhaust requirement applied to Emergency Department Waiting Rooms and to Radiology Waiting Rooms programmed to hold patients who are waiting for chest X-rays for diagnosis of respiratory disease. | Note 2 - Alternative Design. Per ASHRAE Standard 170 - 2013 (or latest approved edition) the design may use HEPA filtration in lieu of 100% exhaust.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Attic Space | NA | NA | 50 | 10 | NA | NA | 10 | 10 | Exhaust (G) | 45 | (o) | Yes | CV |  | Note 1 - Heating System. Provide a thermostatically controlled (closed-loop, local control) heating system utilizing terminal unit heaters or a central heating system. Ensure uniform heat distribution. Minimum outdoor ACH is not required in heating mode. The ventilation system shall be inoperative when the heating system is enabled. | Note 2 - Ventilation System. Provide an exhaust ventilation system (closed-loop, local control either thermostatically or manually operated) to prevent excessive heat build up. The exhaust ventilation system shall consist of exhaust fan(s) and exhaust/intake air louvers with motorized dampers. Provide direct-drive fan(s) to reduce maintenance. If a central, supply air heating system (Note 1) is the selected option, exhaust (relief) arrangement shall be compatible with the central heating system. | Note 3 - Access. Coordinate access to the mechanical equipment with the architectural discipline.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Audiology Instrument Calibration and Repair Shop | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (+) | Yes | VAV
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Battery Charging Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Special Exhaust System. Provide a dedicated, special exhaust system where lead batteries (Automatic Transport System and Wheel Chairs Charging Areas) are charged. Exhaust system is not required where Ni-Cad batteries are charged. Provide a spark-proof construction exhaust fan, explosion-proof motor, and welded stainless steel ductwork. Provide emergency power for the fan motor. Provide local and remote (at ECC) alarm capabilities for fan status and airflow interruption.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Biomedical Instrument Repair Shop | 75 | 24 | 70 | 21 | 60 | 30 | 6 | 2 | Exhaust (S) | 40 | (-) | Yes | CV |  | Note 1 - Dedicated Exhaust System. (a) Provide a dedicated exhaust system where chemicals, such as, xylene and iodine are used. Evaluate the use of a canopy hood or a general purpose fume hood. The system start can be manually operated by a fan switch or automatically operated by remote DDC controls. (b) Provide a spark-proof construction exhaust fan with bearings mounted outside the exhaust air stream and an explosion-proof motor on emergency power. (c) Provide local and remote alarms in the event of fan failure or exhaust airflow interruption. (d) Provide an airflow control valve in the exhaust air duct to ensure constant exhaust airflow. | Note 2 - Alternate Return Air Pick-Up. Provide an alternate return air connection with a motorized damper when the exhaust fan is not in use.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Clean Utility/Storage Room | NA | NA | NA | NA | NA | NA | 4 | NA | Return | 40 | (+) | No | CV |  | Note 1 - HVAC Treatment. (a) For a small, 100 sf [9 m2] and smaller, unoccupied room, individual room temperature control is not required. Room can be supplied from any adjoining constant- volume air terminal unit serving similar interior or perimeter space. Ducted return air pick-up is also not required, as the room air can ex-filtrate into adjoining spaces, such as, a non-exit corridor (NFPA 90A). (b) Individual room temperature control is required for a large, more than 100 sf [9 m2], occupied room. Provide a minimum of 2 ACH outdoor air. | Note 2 - Logistics Service Storage Rooms: (a) For Logistics Service Sterile Consumables (Soft Goods) Storage requirements refer to SRS04: Sterile Consumables (Soft Goods) Storage in Sterile Processing Service Room Data Sheets. (b) For Logistics Service Storage Rooms with non-sterile materials, provide proper room conditions based on the actual materials stored.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Computer Lab Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | VAV
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Copy/Printing Room (Large) | 75 | 24 | 70 | 21 | NA | NA | 6 | 2 | Return | 40 | (o) | Yes | CV
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Copy/Printing Room (Small) | NA | NA | NA | NA | NA | NA | 6 | NA | Exhaust (G) | 40 | (-) | No | CV |  | Note 1 - Usage. Copy/Printing Room (Small) is a local room serving a single department only, with no more than 2 machines. | Note 2 - Conditioning. Conditioned air is drawn from other areas to ventilate the room and reduce the heat load.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Crawl Space (Pipe Basement) | NA | NA | 50 | 10 | NA | NA | 6 | 6 | Exhaust (G) | 45 | NA | Yes | CV |  | Note 1 - Compliance. This space shall comply with PG-18-3 (Design and Construction Procedures), Topic 5 - Pipe Basements, available in the VA Technical Information Library. | Note 2 - Exhaust Ventilation System. Provide a thermostatically-controlled (closed-loop, local control), or manually-operated, exhaust system to minimize excessive heat build-up. The system shall consist of an exhaust fan(s), exhaust air louver, intake louver, and motorized intake and exhaust air dampers (two-position, open/close type). Select a direct-drive exhaust fan to minimize maintenance. | Note 3 - Heating System. Provide thermostatically-controlled (closed-loop, local control) terminal heaters to ensure uniform heat distribution. The ventilation system shall be inoperative when the heating system is enabled.
NON PATIENT ROOMS - MISCELLAENOUS AREAS - Electrical Room | XXXXX | Electrical Equipment Closets without Internal Heat Gain | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - HVAC. Electrical closets without internal heat gain do not require HVAC.
NON PATIENT ROOMS - MISCELLAENOUS AREAS - Electrical Room | XXXXX | Satellite and Main Electrical Rooms with Internal Heat Gain | 86 | 30 | 40 | 5 | NA | NA | NA | Note 2 | Return | 45 | (o) | Yes | CV |  | Note 1 - Equipment Heat Gain. Estimate transformer heat dissipation at the rate of 3% of the anticipated actual peak demand. Do not use the rated nameplate capacity for equipment heat gain. | Note 2 - Mechanical Cooling. (a) Provide a dedicated mechanical cooling unit using chilled water or refrigerant direct expansion (DX) as the cooling medium. Cooling shall be available on demand. (b) Use economizer cycle (ASHRAE Standard 90.1 - 2019 or latest approved version) or exhaust ventilation in mild weather. (c) Provide minimum outdoor air (ASHRAE Standard 62.1 - 2016 or latest approved version) in the mechanical cooling mode. (d) Avoid installing mechanical cooling units within the electrical room to prevent possible damage due to water leakage and/or overflow of condensate drain pans. | Note 3 - Heating. Provide thermostatically-controlled heating system only if the space heat gain cannot offset the design heat loss. | Note 4 - Controls. Provide a DDC sensor to monitor the space temperature and initiate local and remote alarms in the event the space temperature exceeds 95 F [35 C]. DDC sensor for monitoring and alarm is required with local control loop.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Elevator Machine Room | 77 | 25 | NA | NA | NA | NA | NA | NA | Return | 45 | (o) | Yes | CV |  | Note 1 - Equipment Heat Gain. Coordinate equipment heat dissipation with the elevator equipment manufacturer. | Note 2 - Mechanical Cooling Unit. (a) Provide dedicated, thermostatically-controlled mechanical cooling. Use chilled water or direct-expansion (DX) or a dedicated air terminal unit from a nearby air- handling unit in use year-round. (b) Avoid installation of the chilled-water or DX mechanical cooling units within the elevator machine room to prevent possible damage due to water leakage and/or overflowing of the condensate drain pans. | Note 3 - Controls. Provide a DDC sensor to monitor the space temperature and initiate local and remote alarms in the event the space temperature exceeds 95 F [35 C]. DDC sensor for monitoring and alarm is required with local control loop.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Engineering Control Center Room | 75 | 24 | 70 | 21 | 60 | 30 | 4 | 2 | Return | 40 | (o) | Yes | CV |  | Note 1 - HVAC Unit. Provide a dedicated HVAC unit to provide cooling and heating as required using available sources, such as, chilled water, steam or hot water, or a DX cooling unit.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Engineering Shops (Maintenance) | 80 | 27 | 68 | 20 | NA | NA | 6 | 2 | Return Exhaust (G) | 45 | (-) | Yes | CV |  | Note 1 - General. The engineering shops include Carpentry Shop, Electrical Shop, Machine Shop, Paint Shop, Plumbing Shop, and Welding Shop. HVAC requirements and design approach for the shops differ based on the site location (high-humidity or low-humidity) and the specific program requirements. | Note 2 - Room Temperature Control. Provide individual room temperature control for the shops served by mechanical cooling and/or heating systems. Provide mechanical cooling for high-humidity locations and evaluate the use of 100% outdoor air for ventilation for low-humidity locations. | Note 3 - Welding Shop. Provide a dedicated exhaust system for the welding shop. | Note 4 - Paint Shop. For the paint shop, a dedicated exhaust ventilation system may be required to dilute the paint shop fumes. Coordinate with the paint booth supplier if a packaged, dedicated ventilation system is furnished by the paint booth supplier.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Exterior Stairs | NA | NA | 50 | 10 | NA | NA | NA | NA | NA | NA | NA | Yes | NA |  | Note 1 - Heating. Provide a dedicated, thermostatically-controlled terminal heater with closed-loop, non-DDC temperature control.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Housekeeping Aid Closet (HAC) | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Kitchenette | NA | NA | NA | NA | NA | NA | 6 | NA | Exhaust (G) | 40 | (- -) | No | CV
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Litter Storage | NA | NA | NA | NA | NA | NA | 6 | NA | Exhaust (G) | 40 | (- -) | No | CV
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Loading Dock | NA | NA | 60 | 15 | NA | NA | NA | NA | Return | 45 | (o) | Yes | CV |  | Note 1 - Heating System. Provide an air curtain with a heating element. Interlock the air curtain start with the loading dock door operating mechanism. Activate heating when the ambient temperature drops below 45 F [7 C] temperature.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Maintenance Garages | NA | NA | 60 | 15 | NA | NA | - | 100% | Exhaust (S) | 50 | (-) | Yes | CV |  | Note 1 - Ventilation (100% Outdoor Air). Provide a ventilation system complete with fan(s), exhaust and/or supply, and air inlet and outlet connections equipped with motorized dampers. Size and select the system to move air at the rate of 1.5 cfm/sf [7.6 L/s/m2]. | Note 2 - Heating. Provide thermostatically-controlled heat delivered either by the supply air system or individual air terminal units. During heating mode, reduce the outdoor air to minimum as mandated by ASHRAE Standard 62.1-2016 or latest approved edition and other applicable documents. | Note 3 - Compliance and Reference. The HVAC system shall be in compliance with the American Council of Government Industrial Hygienists (ACCIH) and NFPA 88B. Refer to the ASHRAE Handbook of Applications for further information.
NON PATIENT ROOMS - MISCELLAENOUS AREAS - Mechanical Equipment Room | XXXXX | Air Handling Equipment Rooms | 84 | 29 | 50 | 10 | NA | NA | 6 | 2 | Return | 45 | (o) | Yes | CV |  | Note 1 - HVAC (All Locations). Provide a dedicated supply air takeoff (from the air-handling unit located in the MER) to circulate conditioned air at 0.5 cfm/sf [2.5 L/s/m2]. Circulated air can be returned back to the unit. Thermostatically-controlled terminal heater may be required to maintain the winter set point, where the AHU is not in operation round- the-clock.
NON PATIENT ROOMS - MISCELLAENOUS AREAS - Mechanical Equipment Room | XXXXX | Heating Rooms | 86 | 30 | 40 | 5 | NA | NA | 6 | 2 | Return | 45 | (o) | Yes | CV |  | Note 1 - Heating Rooms. Heating Rooms are the designated mechanical equipment rooms where steam enters the building for space heating, domestic hot water production, process heating, etc. The Heating Room is equipped with heat exchangers, PRV stations, circulating pumps, and other steam and hot water specialties. | Note 2 - High Humidity Locations. (a) HVAC Systems. Provide mechanical cooling, during peak summer season, by a thermostatically-controlled, dedicated chilled water or direct-expansion (DX) unit. The room can also be served by a thermostatically-controlled, air terminal unit from a nearby air-handling unit in operation round-the-clock. (b) Heating Requirement. Verify the need for heating. Generally heating is not required as the heat produced within the space is sufficient enough to maintain above freezing temperatures. | Note 3 - All Other Locations. (a) Ventilation Option. For low-humidity (dry) locations, in mild weather, exhaust and/or supply air ventilation system can be used to keep the space temperature below 86 F [30 C]. The system shall consist of fans, inlet and outlet connections with motorized dampers, ductwork, and thermostatic controls. If using this option, increase minimum total ACH to 10. (b) Mechanical Cooling. Provide mechanical cooling, during peak summer season, by a thermostatically-controlled, dedicated chilled water or DX unit. The room can also be served by a thermostatically-controlled, air terminal unit from a nearby air-handling unit in operation round-the-clock. (c) Heating. Verify the need for heating. Generally heating is not required as the heat produced within the space is sufficient enough to maintain above freezing temperatures.
NON PATIENT ROOMS - MISCELLAENOUS AREAS - Mechanical Equipment Room | XXXXX | Refrigeration Equipment Rooms | 86 | 30 | 40 | 5 | NA | NA | 6 | NA | Return | 45 | (o) | Yes | CV |  | Note 1 - High Humidity Locations. (a) General. Provide a dedicated mechanical cooling unit, complete chilled water or direct-expansion (DX) coil and minimum MERV 7 filters. Provide minimum outdoor air per ASHRAE Standard 15 (latest edition) and capability to operate at 100% outdoor air during emergency refrigerant evacuation mode. Provide a variable speed drive to facilitate system operation in the normal and emergency modes. (b) Capacity - Mechanical Cooling Unit. Base the capacity on the maximum of: Internal heat gain (note that the heat dissipated by open chillers is much higher than hermetic chillers) Exhaust air volume required to dilute the refrigerant spill - see ASHRAE Standard 15 - 2016 or latest approved version. | Note 2 - All Other Locations. Provide a refrigerant leak detection system complete with field-installed refrigerant detection sensors, wiring and local control panel per ASHRAE Standard 15 - 2016 or latest approved edition. Provide an open protocol BACnet interface with the building ECC system. Provide local alarms per ASHRAE Standard 15 - 2016 or latest approved edition requirements. Provide remote alarms at the ECC. | Note 3 - Emergency Refrigerant Leak Evacuation System. Provide a refrigerant leak detection system complete with field-installed refrigerant detection sensors, wiring and local control panel per ASHRAE Standard 15 - 2016 or latest approved edition. Provide an open protocol BACnet interface with the building ECC system. Provide local alarm requirements per ASHRAE Standard 15 -2016 or latest approved edition. Provide remote alarms at the ECC. | Note 4 - Emergency Exhaust System. Upon activation by the leak detection system, the room air shall be exhausted outdoors by an emergency exhaust system and supply air system shall operate in 100% outdoor air mode. Provide exhaust air inlets in accordance with the recommendations of ASHRAE Standard 15 - 2016 or latest approved edition and chiller manufacturer. Activation of the leak detection system shall also trigger local and remote alarms. Provide emergency power for the emergency exhaust and supply fans and associated controls.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Reagent Grade Water Treatment Room | 75 | 24 | 70 | 21 | 60 | 30 | 8 | 2 | Exhaust (G) | 40 | (-) | Yes | CV
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Soiled Utility and Storage Room | NA | NA | NA | NA | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | No | CV
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Standby Generator Room | 80 | 29 | 40 | 18 | NA | NA | 4 | NA | Return | NA | (o) | Yes | CV |  | Note 1 - Design Requirements. Design requirements listed above are for when the engine is not operating. During engine operation, exhaust air is required and room air balance is negative. During operation, room temperature shall not exceed maximum ambient temperature recommended by engine manufacturer. | Note 2 - Damper Requirements. Provide motorized dampers for all louvers. Dampers shall fail-open on loss of power. | Note 3 - Analysis Requirement. (a) Submit a detailed analysis showing all options and systems selected to provide proper ventilation and cooling of the standby generator space. (b) Numerous design considerations must be included in the analysis. Once the size of the generator plant has been determined and the number of units selected then various manufacturers shall be consulted to ascertain the range of heat rejection from the various components. See Figure 6-1, Standby Generator Room, for the average heat rejection values. Assuming the prime movers are reciprocating diesel engines, consideration shall be given to the required radiator flow rates when the unit is naturally aspirated, turbocharged or is a lean burn unit. Airflow rates required for unit mounted radiators can vary substantially from one type to another and manufacturer to manufacturer. | Note 4 - Configuration Options. a) The electrical equipment including the generator and onboard or nearby electrical equipment can be specified for wet locations, or remote radiators can be used thereby drastically reducing the louver area requirement. (b) A system with a mix of unit mounted radiators and remote units can be proposed. (c) The analysis shall compare unit mounted radiators to remote radiators. The analysis shall include cost of louvers and control devices. Louvers in areas prone to hurricanes or wind-debris hazards shall be meet the following Florida Building Code tests: Uniform Static Air Pressure Test, Cyclic Wind Pressure Test, Large Missile Impact Test, and Wind Driven Rain Resistance Test for Dry Areas, Enclosed. (d) A separate detailed acoustic analysis shall be submitted for the final design of the standby generator facility. | Note 5 - Design Considerations. (a) The switchgear and control rooms shall be fully air-conditioned. If remote radiators are used and only minimal louvers are required for combustion air ventilation, consideration should be given to air conditioning the engine bay. The louvers are fitted with electrically controlled actuators to open as needed. Do not provide air conditioning during operation of the generator. (b) If remote radiators are used, consideration of glycol addition to the system is required in freezing areas. (c) Engine exhaust must be safely conveyed from the engine through the piping and any auxiliary equipment to the atmosphere within allowable pressure drops. (d) Maintain separate exhaust for each engine. Provide individual silencers or mufflers for each exhaust system. (e) Exhaust systems shall use welded tube turns with radius of 4 pipe minimum diameters. (f) See VA Master Specification 26 32 13 ENGINE GENERATORS for additional information.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Trash Collection Room | NA | NA | 50 | 10 | NA | NA | 10 | NA | Exhaust (G) | 40 | (- -) | Yes | CV |  | Note 1 - Exhaust System. Provide a dedicated general exhaust system, if a common general exhaust system is not available in the vicinity. Exhaust system shall be manually operated and shall run continuously. | Note 2 - Heating. Provide a thermostatically-controlled heating system if wet sprinkler piping and/or any other building service piping passes through the room.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Vestibules | NA | NA | 50 | 10 | NA | NA | NA | NA | NA | 40 | (+) | Yes | CV |  | Note 1 - Heating. Provide a thermostatically-controlled terminal heater. Coordinate heater type and location with the architectural discipline. Floor-mounted cabinet unit heaters with bottom horizontal supply and top return have proven effective in counter-acting cold air settling at the floor level. Heating for vestibules and for air curtains with integral heating shall include automatic controls capable of and configured to shut off the heating system when outdoor air temperatures are above 45°F. | Note 2 - Space Pressurization. Supply 1.0 cfm/sf [5.1 L/s/m2] air under positive pressure from an adjoining air terminal unit serving the lobby to maintain positive air pressure by allowing air to ex- filtrate outdoors. | Note 3 - Vestibule heating and cooling systems controls shall be capable of and configured to limit heating to a maximum of 60°F and cooling to a minimum of 85°F.
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Walk-in Refrigerator and Freezers | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Note 1 - Specifications. Coordinate equipment installation and design with the VA Master Specifications and Standard Details. Revised specifications are: Walk-In Coolers and Freezers - Section 11 41 21, Laboratory Refrigerators - Section 11 53 23, and Mortuary Refrigerators - Section 11 78 13. | Note 2 - Constant Temperature Rooms. Rooms covered under VA Master Specification Section 13 21 29 are used for laboratories and research facilities. Generally, the mechanical contractor does not furnish these items. Provide DDC temperature sensors for these rooms to sound local and remote alarms at the ECC. Provide ventilation air requirements per ASHRAE 62.1 - 2016 or latest approved edition only if building is pursuing LEED certification. | Note 3 - Frost Prevention. Include provisions to prevent frost formation and subsequent floor heating for equipment mounted on grade or above grade with fill. Provide heating cables in coordination with the electrical discipline to prevent freezing below grade or concrete sub-floor. Evaluate the possibility of using waste heat for anti-frost system, to conserve energy. | Note 4 - Emergency Power. Provide emergency power for the equipment and controls serving refrigerators and freezers. | Note 5 - Heat Gain Factors. Use ASHRAE recommendations for heat gain factors, load calculations and compressor running time while selecting equipment to maintain the temperatures listed below: Dairy Freezers: -20 F [-29 C], Ice Cream Freezers: -20 F [-29 C] Meat Freezers: -12 F [-24 C], Fresh Meat Refrigeration: 32 F [0 C] Walk-In Refrigerators: 36 F [2 C], Autopsy (Mortuary) Cold Room: 36 F [2 C] Subsistence Storage (Supply Service): 36 F [2 C]
NON PATIENT ROOMS - MISCELLAENOUS AREAS | XXXXX | Warehouse (Central) with Pharmacy | 80 | 27 | 68 | 20 | 60 | NA | 4 | 2 | Return | 45 | (o) | Yes | VAV |  | Note 1 - HVAC Systems - Warehouse. Provide mechanical cooling and heating for high-humidity locations. Provide ventilation and heating for all other locations. Base the system selection on the warehouse size and availability of the utilities. With the mechanical cooling option, provide two sets of pre-filters (MERV 7 and 11). With the ventilation option, MERV 7 pre-filter can be used. | Note 2 - HVAC Systems - Pharmacy. Provide a thermostatically-controlled mechanical cooling unit to maintain 75 F [24 C] with 60% RH in cooling mode and 70 F [21 C] with 30% RH in heating mode.

## AHU Data Sheets
ATTRIBUTE - 08/01/2023 | ATRIUM | AUDITORIUMS AND THEATERS | AUTOPSY SUITE | BIOMEDICAL LABORATORY RESEARCH AND DEVELOPMENT (BLR&D) | CARDIOVASCULAR LAB SERVICE | CLINICAL SERVICES RESEARCH & DEVELOPMENT (CSR&D) | COMMUNITY LIVING CENTER | CENTRAL LAUNDRY FACILITY | DENTAL CLINIC SPACES | DIALYSIS TREATMENT SPACES | DIGESTIVE DISEASES ENDOSCOPY SUITE | DINING AREA (CAFETERIA) | DOMICILIARY | ELECTROENCEPHALOGRAPHY LABORATORY (EEG) SPACES | EMERGENCY DEPARTMENT | EYE CLINIC SPACES | GYMNASIUM | HEALTH SERVICES RESEARCH & DEVELOPMENT (HSR&D) | IMAGING SERIES | INFECTIOUS ISOLATION ROOMS / PROTECTIVE ENVIRONMENTS | KITCHEN (FOOD PRODUCTION) | PATHOLOGY & LABORATORIES | MAIN ENTRANCE LOBBY | INPATIENT MENTAL HEALTH UNIT | MENTAL HEALTH REHABILITATION TREATMENT PROGRAM FACIILITY | OUTPATIENT MENTAL HEALTH SERVICES | NURSING WING | OIT MAIN COMPUTER ROOM | OIT SATELLITE | PATIENT CARE AREAS | PHARMACY SERVICE | POLYTRAUMA REHABILITATION CENTER INPATIENT NURSING UNIT | POLYTRAUMA OUTPATIENT UNIT | PULMONARY MEDICINE SERVICE | R&D COMMON AREAS (FRONT OR BACK) | R&D NON-PROFIT (N-P) | REHABILITATION RESEARCH & DEVELOPMENT UNIT (RRDU) | SPINAL CORD INJURY/DISORDERS CENTER | STANDALONE SMOKING FACILITY | STERILE PROCESSING SERVICES (SPS) | SURGICAL SUITE | VETERINARY MEDICAL UNIT (VMU) | MINIMUM VENTILATION AIR | NON-PATIENT CARE AREAS
Air Handling Type | Dedicated (paragraph 6.2). Constant or Variable Air Volume | Dedicated (paragraph 6.2). Constant or Variable Air Volume | Dedicated Medium Pressure Constant Volume (paragraphs 3.2.3 and 6.2) | Dedicated (Par 6.2) or Non-dedicated (Par 6.3) [see Note 1] Constant and Variable Air Volume (Par 3.2.3) | Dedicated Variable Air Volume or Medium Pressure Constant Volume (paragraphs 3.2.3, 6.2 and 6.3) | Non-dedicated (Par 6.3) Variable Air Volume | Non-dedicated Variable Air Volume (paragraphs 3.2.3, 6.3 and 6.4) | Dedicated (paragraph 6.2). Constant Volume / Variable Volume | Dedicated Variable Air Volume (paragraphs 3.2.3, 6.2 and 6.4) | Dedicated or Non-dedicated Variable Air Volume (paragraphs 3.2.3, 6.2, 6.3 and 6.4) | Dedicated Variable Air Volume or Medium Pressure Constant Volume (paragraphs 3.2.3, 6.2, 6.3 and 6.4) | Dedicated Variable Air Volume (paragraphs 3.2.3 and 6.2) | Dedicated or Non-dedicated Variable Air Volume (paragraphs 3.2.3, 6.2, 6.3 and 6.4) | Non-dedicated (Par 6.3) Variable Air Volume | Dedicated Variable Air Volume (paragraphs 3.2.3, 6.2 and 6.4) | Non-dedicated (Par 6.3) Variable Air Volume | Dedicated (Par 6.2) Constant Volume | Non-dedicated (Par 6.3) Variable Air Volume | Dedicated Variable Air Volume (paragraphs 3.2.3, 6.2 and 6.4) | Non-dedicated Variable Air Volume or Medium Pressure Constant Volume (paragraphs 3.2.3, 6.3 and 6.4) | Dedicated Constant Volume (paragraphs 3.2.3, 6.2 and 6.4) | Dedicated (Par 6.2) Variable Air Volume | Dedicated Variable Air Volume (paragraphs 3.2.3, 6.2 and 6.4) | Non-dedicated Variable Air Volume (paragraphs 3.2.3, 6.3 and 6.4) | Non-dedicated (Par 6.3)Variable Air Volume | Non-dedicated (Par 6.3) Variable Air Volume | Dedicated Variable Air Volume (paragraphs 3.2.3, 6.2 and 6.4) | Dedicated (Par 6.2) Constant Volume | Dedicated or Non-Dedicated (Par 6.2 and 6.3), Constant Volume or Variable Volume | Non-dedicated (Par 6.3) Variable Air Volume | Dedicated (paragraph 6.2) Variable Air Volume | Dedicated Variable Air Volume (paragraphs 3.2.3, 6.2 and 6.4) | Non-dedicated (Par 6.3) Variable Air Volume | Non-dedicated (par 6.3) Variable Air Volume | Non-dedicated (Par 6.3) Variable Air Volume | Non-dedicated (Par 6.3) Variable Air Volume | Non-dedicated (Par 6.3) Variable Air Volume | Dedicated Variable Air Volume (paragraphs 3.2.3, 6.2 and 6.4) | Dedicated (Par 6.2) Constant Volume | Dedicated (Par 6.2) Variable Air Volume | Dedicated Variable Air Volume (paragraphs 3.2.3, 6.2 and 6.4) | Dedicated (paragraph 6.2) Constant Volume - With Supply and Exhaust Terminals for zone temperature and pressure control | Non Dedicated (Par 6.3) Constant Volume | Non-dedicated (Par 6.3) Variable Air Volume
Indoor Design Temperature - Cooling | 75 F [24 C] | 75 F [24 C] | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 75 F [24 C] | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 75 F [24 C] | Room Data Sheets | Room Data Sheets | Room Data Sheets | 78 F [26 C] | Room Data Sheets | 75 F [24 C] | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 77 F [25 C] | Room Data Sheets | Room Data Sheets | Room Data Sheets | Not Applicable | Room Data Sheets
Indoor Design Temperature - Heating | 70 F [21 C] | 70 F [21 C] | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 70 F [21 C] | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 70 F [21 C] | Room Data Sheets | Room Data Sheets | Room Data Sheets | 70 F [21 C] | Room Data Sheets | 70 F [21 C] | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 70 F [21 C] | Room Data Sheets | Room Data Sheets | Room Data Sheets | Not Applicable | Room Data Sheets
Indoor Design Relative Humidity - Dehumidification | 60% | 60% | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 60% | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 60% | Room Data Sheets | Room Data Sheets | Room Data Sheets | 60% | Room Data Sheets | 60% | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 60% | Room Data Sheets | Room Data Sheets | Room Data Sheets | 60% RH | Room Data Sheets
Indoor Design Relative Humidity - Humidification | Optional (30%) | Optional (30%) | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Optional (30%) | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Optional (30%) | Room Data Sheets | Room Data Sheets | Room Data Sheets | Not Required | Room Data Sheets | Optional (30%) | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Not Required | Room Data Sheets | Room Data Sheets | Room Data Sheets | 30% RH | Room Data Sheets
Minimum Total Air Changes Per Hour | 4 | 4 | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 6 | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 6 | Room Data Sheets | Room Data Sheets | Room Data Sheets | 10 | Room Data Sheets | 6 | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Based on Unit Capacity | Based on Unit Capacity | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | 6 | Room Data Sheets | Room Data Sheets | Room Data Sheets | Not Applicable | Room Data Sheets
Minimum Outdoor Air Changes Per Hour | 2 | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | 100% | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | 100% | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | ASHRAE Standard 62.1 - 2016 or latest approved edition. | ASHRAE Standard 62.1-2016 or latest approved edition. | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets | 100% | Chapter 2 and Room Data Sheets | Chapter 2 and Room Data Sheets
Return Air Permitted | Yes (Normal Mode) | Yes | No | No | Yes | Yes | Yes (Normal Mode) | Room Data Sheets | Yes (Normal Mode) | Yes (Normal Mode) | Yes (Normal Mode) | Yes | Yes (Normal Mode) | Yes | Yes (Normal Mode) | Yes | Yes | Yes | Yes (Normal Mode). Also, see Room Data Sheets | Yes (Normal Mode). Also, see Room Data Sheets | Yes (Normal Mode) | No | Yes (Normal Mode) | Yes (Normal Mode) | Yes | Yes | Yes (Normal Mode) | Yes | Yes | Yes | Yes | Yes (Normal mode) | Yes | Yes | Yes | Yes | Yes | Yes (Normal Mode) | Yes | No | Yes (Normal Mode) | No | No | Yes
Exhaust Air Required | Yes (Smoke Evacuation Mode) | No | Yes | Yes | No | No | Yes (Emergency Mode) | Room Data Sheets | Yes (Emergency Mode). Also, see Room Data Sheets | Yes (Emergency Mode). Also, see Room Data Sheets | Yes (Emergency Mode). Also, see Room Data Sheets | Yes | Yes (Emergency Mode) | See Room Data Sheets | Yes (Emergency Mode) Also, see Room Data Sheets | See Room Data Sheets | No | No | Yes (Emergency Mode). Also, see Room Data Sheets | Yes (Emergency Mode). Also, see Room Data Sheets | Yes | Yes | Yes (Emergency Mode). Also, from Selected Spaces | Yes (Emergency Mode) | No | No | Yes (Emergency Mode) | No | No | No | Yes | Yes (Emergency mode) | No | No | No | No | No | Yes (Emergency Mode) | Yes (Intermittently) | Yes | Yes (Emergency Mode) | Yes | Yes | No
Air Economizer Cycle Required | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | Not Applicable | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | No | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | ASHRAE Standard 90.1 - 2019, or latest approved edition. | No | ASHRAE Standard 90.1 - 2019, or latest approved edition. | Not Applicable | Not Applicable | ASHRAE Standard 90.1 - 2019, or latest approved edition.
Energy Recovery System Required | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS. Also, see Note 2 | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | No | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS | See paragraphs 3.6 through 3.6.4 ENERGY RECOVERY SYSTEMS
Filtration - Pre-Filters (PF-1 and PF-2) | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 14 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | Manufacturer's Standard | Manufacturer’s Standard | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF 1 = MERV 7 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 11 | PF-1 = MERV 7 and PF-2 = MERV 14
Filtration - After-Filters (AF) | None | None | None | None | AF = MERV 14 (Normal Mode) AF = MERV 16A (Emergency Mode) | None | None | None | AF = MERV 14 | AF = MERV 14 | AF = MERV 14 | None | None | AF = MERV 14 (Normal Mode) AF = MERV 16A (Emergency Mode) | AF = MERV 14 | AF = MERV 14 (Normal Mode) AF = MERV 16A (Emergency Mode) | None | None | AF = MERV 14 | AF = MERV 14 | None | None | None | AF = MERV 14 | AF = MERV 14 (Normal Mode) AF = MERV 16A (Emergency Mode) | AF = MERV 14 (Normal Mode) AF = MERV 16A (Emergency Mode) | AF = MERV 14 (See Note 4 below) | None | None | AF = MERV 14 (Normal Mode) AF = MERV 16A (Emergency Mode) | None | AF = MERV 14 | AF = MERV 14 (Normal Mode) AF = MERV 16A (Emergency Mode) | AF = MERV 14 (Normal Mode) AF = MERV 16A (Emergency Mode) | None | None | None | AF = MERV 14 | None | AF = MERV 14 | AF = MERV 14 | AF = MERV 14 | None | None
Filtration - Final-Filter (FF) | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | FF = MERV 14 (Normal Mode) FF = MERV 16A (Emergency Mode) | None | None | None | None | None | None | None | None | None | See Note 10 | None | None | None
Cooling Source | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water, DX, Evap Cooling | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water or DX | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water or DX | Chilled Water or DX | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water or DX | Chilled Water | Chilled Water | Chilled Water | Chilled Water | Chilled Water
Heating Source | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Hot Water or Steam | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Hot Water | Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water, Electric | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water | Steam and/or Hot Water
Humidification Source | Plant or "Clean" Steam | Plant or "Clean" Steam | Plant or "Clean" Steam | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant or "Clean" Steam | Plant or "Clean" Steam | Plant Steam or "Clean Steam" | Plant or "Clean" Steam | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant or "Clean" Steam | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant or "Clean" Steam | Plant or "Clean" Steam | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Not Required | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or Clean Steam | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant or "Clean" Steam | Plant or "Clean" Steam | Plant or "Clean" Steam | Plant Steam or "Clean Steam" | Not Required | Plant Steam or "Clean Steam" | Plant Steam or "Clean Steam" | Plant Steam or "Clean" Steam | Plant or "Clean" Steam | Plant or "Clean" Steam
General Exhaust System Required | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Room Data Sheets | Room Data Sheets | Yes | Yes | Yes | Room Data Sheets | Yes | Room Data Sheets | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Special Exhaust System Required | Yes (Smoke Evacuation Mode) | No | Yes | Yes | No | Room Data Sheets | Room Data Sheets | Yes | Room Data Sheets | Room Data Sheets | No | Yes | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | No | Room Data Sheets | Yes | Yes | Yes | Yes | No | No | No | No | Yes (Emergency Mode) | No | No | No | Yes | Yes (Emergency mode) | No | No | Room Data Sheets | No | Room Data Sheets | No | No | Yes | Yes (Emergency Mode) | Yes | No | Room Data Sheets
Emergency Power Required | Yes (Smoke Evacuation System) | No | Yes (Exhaust System Only) | Yes | No | Yes | Yes | No | No | No | No | No | Yes | No | Yes | No | No | Yes | MRI Unit, Emergency Exhaust Fan, Associated Controls | Yes - Equipment Branch | No | Yes | No | No | No | No | Yes | Yes For Unit and Controls | Yes For Unit and UPS for Controls | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes
Individual Room Temperature Control Required | Yes | Yes | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Yes | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Yes | Room Data Sheets | Room Data Sheets | Room Data Sheets | Yes | Room Data Sheets | Yes | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Yes | Yes | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Yes | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets
Room Air Balance | Positive (+) (Normal Mode) , Negative (-) (Smoke Evacuation) | Positive (+) | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Negative (-) | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Neutral (o) | Room Data Sheets | Room Data Sheets | Room Data Sheets | Negative (-) | Room Data Sheets | Positive (+) | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Positive (+) | Positive | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Negative (-) | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets | Room Data Sheets
Compliance | AAALAC and NIH DRM | None | None | NFPA 45 and 99 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | NFPA 96 | NFPA 45 and 99 | None | None | None | None | None | None | None |  | USP <797> and USP <800> | None | None | None | None | None | None | None | None | None | NFPA 99 | AAALAC and NIH DRM | None | None
Note 1 | Note 1 - HVAC System Based on Atrium configuration and air distribution arrangement, evaluate using a variable air volume HVAC system in lieu of a constant volume system. | Note 1 - HVAC System Based on Auditorium and Theater air distribution arrangement and extent of conditioned air volume, evaluate using a variable air volume HVAC system in lieu of a constant volume system. | Note 1 - Dedicated Air-Handling Unit A dedicated air-handling unit for the Autopsy Suite is NOT required if a 100% OA air-handling unit in the vicinity can meet the requirements of the hours of operation and filtration. | Note 1 - Air-Handling Unit. A dedicated air-handling unit with 100% outdoor air is required when a group of laboratories, forming a full-fledged department is in the project scope. One or two laboratories, in the outpatient clinic or similar facilities, can be served by an air-handling unit with minimum outdoor air shown in the Room Data Sheets (Reference: ASHRAE Standard 170-2016 or latest approved edition) and meeting the filtration requirements. | Note 1 - General Depending on the size of the Cardiovascular Lab Service area, the space may be served by a non-dedicated air handling unit as long as the unit meets all the minimum requirements described herein. | Note 1 - VAV Air-Handling Units. The all-air VAV system describe here can be used for applicable spaces such as offices, lobbies, classrooms, examination rooms, conference rooms, etc. The number of air handling units shall be determined by practical design considerations such as available mechanical room spaces, available above ceiling space for ductwork, functional space grouping, occupancy schedules etc. Spaces requiring constant volume shall be served by constant volume air terminals. | Note 1 - VAV Air-Handling Units The all-air VAV system describe here can also be used for applicable spaces such as offices, lobbies, classrooms, examination rooms, conference rooms, etc. The number of air handling units shall be determined by practical design considerations such as available mechanical room spaces, available above ceiling space for ductwork, functional space grouping, occupancy schedules etc. Spaces requiring constant volume shall be served by constant volume air terminals. | Note 1 - Listed Rooms and Their Names In RDS Sheets Since a current VA design guide is a not available, the listed rooms, their names, and the design conditions are based on research for compliance with ASHRAE, American Conference of Governmental Industrial Hygienists Industrial Ventilation Manual, and past VA HVAC Design Manual. | Note 1 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 1 - Dedicated Air-Handling Unit A dedicated air-handling unit is required if the AHU serving Dialysis Treatment and other spaces is not capable of operating at 100% OA during emergency epidemic mode, or if the AHU does not meet the requirements of the hours of operation and filtration. If warranted for other reasons the dialysis clinic may be provided with its own dedicated air handling unit. | Note 1 - Dedicated Air-Handling Unit A dedicated air-handling unit is required if the AHU serving Digestive Health and other spaces is not capable of operating at 100% OA during emergency epidemic mode, or if the AHU does not meet the requirements of the hours of operation and filtration. | Note 1 - Kitchen Make-Up Air Estimate the make-up air requirement for the adjoining kitchen (if any) and transfer room air to the kitchen. Maintain the dining or cafeteria under positive air balance with respect to the kitchen. | Note 1 - VAV Air-Handling Units. The all-air VAV system describe here can also be used for applicable spaces such as offices, lobbies, classrooms, examination rooms, conference rooms, etc. The number of air handling units shall be determined by practical design considerations such as available mechanical room spaces, available above ceiling space for ductwork, functional space grouping, occupancy schedules etc. Spaces requiring constant volume shall be served by constant volume air terminals. | Note 1 - General. A separate air handling unit is not required and not prohibited. Any air handling unit used must meet the minimum requirements listed. If warranted for other reasons the EEG Laboratory may be provided with its own dedicated air handling unit. | Note 1 - Listed Rooms and Their Names. Room name and criteria shown in attached Room Data Sheets (RDS) are based on VA PG 18-12 Emergency Services Design Guide. | Note 1 - General A separate air handling unit is not required and not prohibited. Any air handling unit used must meet the minimum requirements listed. If warranted for other reasons the Eye Clinic may be provided with its own dedicated air handling unit. | Note 1 - Demand-Controlled Ventilation Incorporate demand-controlled ventilation sequence, if feasible, to control outdoor air based on carbon-dioxide concentration. Follow requirements of ASHRAE Standard 62.1 - 2016 or latest approved edition. | Note 1 - VAV Air-Handling Units. The all-air VAV system describe here can be used for applicable spaces such as offices, lobbies, classrooms, examination rooms, conference rooms, etc. The number of air handling units shall be determined by practical design considerations such as available mechanical room spaces, available above ceiling space for ductwork, functional space grouping, occupancy schedules etc. Spaces requiring constant volume shall be served by constant volume air terminals. | Note 1 - Listed Rooms and Their Names Room names shown in the attached Room Data Sheets are based on the VA Radiology Service Design Guide, April 2008; the VA MRI Design Guide, April 2008; the VA Radiation Therapy Service Design Guide, April 2008; and the VA Nuclear Medicine Design Guide April 2008. See other sections of Chapter 6 for the miscellaneous and support rooms, such as, Housekeeping Aide's Closet (HAC), Attic Space, Crawl Space (Pipe Basement), Exterior Stairs, Mechanical/Electrical Rooms, etc. | Note 1 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode | Note 1 - Space Air Balance Minimum room air changes can be increased to meet the exhaust requirements of the range hood and canopy hoods. Conversely, room air can be returned back to the air-handling unit if the system air balance shows surplus air after accounting for the hood exhaust requirement and the use of the return air is economically viable. Transfer air from the exit corridor may be used to maintain negative air balance in the space. | Note 1 - Air-Handling Unit A dedicated air-handling unit with 100% outdoor air is required when a group of laboratories, forming a full-fledged department is in the project scope. One or two laboratories, in the outpatient clinic or similar facilities, can be served by an air-handling unit with minimum outdoor air shown in the Room Data Sheets (Reference: ASHRAE Standard 170-2016 or latest approved edition) and meeting the filtration requirements. | Note 1 - Areas Served The air-handling unit may serve adjoining spaces, such as, Gift Shop, Barber's Shop, Chapel, Public Toilets, and Waiting and Admitting. See Non Patient Room Data Sheets, for additional information on these spaces. | Note 1 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 1 - General A separate air handling unit is not required and not prohibited. Any air handling unit used must meet the minimum requirements listed. The air handling unit must operate 24 hours per day, 7 days per week. | Note 1 - General A separate air handling unit is not required and not prohibited. Any air handling unit used must meet the minimum requirements listed. The air handling unit must operate 24 hours per day, 7 days per week. | Note 1 - Listed Rooms and Their Names The space types listed in this manual reflect the terminology and functions used in the VA Medical/Surgical Inpatient Units and Intensive Care Nursing Unit Design Guide dated November 29, 2011. | Note 1 - Standby Capacity Provide N+1 computer room air-conditioning units. N = Number of units in operation required to meet the load and 1 is the standby unit of capacity equal or greater than the largest of the N units. | Note 1 – General HVAC for telephone and satellite OIT spaces must be provided by systems adjacent to the space if they are systems capable of providing cooling 24/7 365 per year. Systems that do not operate 24/7 or which switch to heating a times during the year cannot be used. In such cases provide local cooling by the most practical method. | Note 1 - General In general, the patient care areas in the Room Data Sheets (RDS) which follow do not require a separate air handling unit. However, if other reasons such as energy, economics, building layout or other similar concerns make a separate air handling unit advantageous, a separated dedicated air handling unit may be provided. Any air handling unit used must meet the minimum requirements listed. | Note 1 - Listed Rooms and Their Names Room names shown in the attached Room Data Sheets are based on Chapter 268: Pharmacy Service in PG-18-9 Space Planning Criteria dated March 2008 and revised October 3, 2016. Since the VA Pharmacy Design Guide Currently in the TIL dates back to 1998 which predates space codes and the current versions of USP 797 and USP 800 that document was not referenced for this HVAC Design Manual. See other tables in chapter 6 for general support areas such as staff and patient toilets and housekeeping aid closets (HAC), locker rooms, lounges, etc. | Note 1 - General - Handling Unit Provide a dedicated air-handling unit where the Polytrauma Rehabilitation Center is constructed as a standalone entity or full-fledged department. The air-handling unit can also serve the Polytrauma Transitional Rehabilitation Program unit (PTRP) unit if located in the same building. The air handling unit shall be served by equipment branch of emergency power. | Note 1 - General A separate air handling unit is not required and not prohibited. Any air handling unit used must meet the minimum requirements listed. The air handling unit must operate on the same schedule as the outpatient unit. | Note 1 - General A separate air handling unit is not required and not prohibited. Any air handling unit used must meet the minimum requirements listed. | Note 1 - VAV Air-Handling Units. A dedicated air-handling unit with 100% outdoor air is required when a group of laboratories, forming a full-fledged department is in the project scope. One or two laboratories, in the outpatient clinic or similar facilities, can be served by an air-handling unit with minimum outdoor air shown in the Room Data Sheets (Reference: ASHRAE Standard 170-2013 or latest approved edition) and meeting the filtration requirements. | Note 1 - VAV Air-Handling Units. A dedicated air-handling unit with 100% outdoor air is required when a group of laboratories, forming a full-fledged department is in the project scope. One or two laboratories, in the outpatient clinic or similar facilities, can be served by an air-handling unit with minimum outdoor air shown in the Room Data Sheets (Reference: ASHRAE Standard 170-2013 or latest approved edition) and meeting the filtration requirements. | Note 1 - VAV Air-Handling Units. A dedicated air-handling unit with 100% outdoor air is required when a group of laboratories, forming a full-fledged department is in the project scope. One or two laboratories, in the outpatient clinic or similar facilities, can be served by an air-handling unit with minimum outdoor air shown in the Room Data Sheets (Reference: ASHRAE Standard 170-2016 or latest approved edition) and meeting the filtration requirements. | Note 1 - General Provide a dedicated air-handling unit where the Spinal Cord Injury/Disorders Center (SCI) is constructed as a standalone entity or full-fledged department. The air-handling unit can also serve the SCI Long Term Care unit if located in the same building. The air handling unit shall be served by equipment branch of emergency power. | Note 1 - VHA Directive Per VHA Directive (2003-035 dated July 1, 2003), smoking is permitted for long term care patients and mental health patients. Indoor smoking must not interfere with the safety of non-smokers. | Note 1 - Listed Rooms and Their Names Room names and criteria shown in the attached Room Data Sheets are based on the VA Design Guide for Logistics Service and Sterile Processing Services dated October 1, 2015 on Chapter 285: Sterile Processing Service in PG-18-9 Space Planning Criteria dated March 2008 and revised October 3, 2016; and on VHA Directive 1116 dated March 23, 2016. See other sections of Chapter 6 for the miscellaneous and support rooms, such as, Housekeeping Aide's Closet (HAC), Attic Space, Crawl Space (Pipe Basement), Exterior Stairs, Mechanical/Electrical Rooms, etc. | Note 1 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on the VA Surgical Service Design Guide dated April 2016. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 1 - Listed Rooms and Their Names In RDS Sheets. Since current VA design guides are a not available the listed rooms, their names, and the design conditions are based on research for compliance with the American Association for Accreditation of Laboratory Animal Care (AAALAC) and the National Institute of Health Design Requirement Manual (NIH DRM). | Note 1 - Application The minimum ventilation air unit is used when spaces are served by heating and cooling terminal units, such as, fan coil units, ground source heat pumps, etc. | Note 1 - VAV Air-Handling Units The all-air VAV system describe here can be used for applicable spaces such as offices, lobbies, classrooms, examination rooms, conference rooms, etc. The number of air handling units shall be determined by practical design considerations such as available mechanical room spaces, available above ceiling space for ductwork, functional space grouping, occupancy schedules etc. Spaces requiring constant volume shall be served by constant volume air terminals.
Note 2 | Note 2 - Smoke Evacuation System Design the smoke evacuation system per NFPA 101 and its associated documents. VA has opted to follow NFPA 101 with the understanding that the provisions of NFPA 101 may be at variance with the IBC. The design calculations shall be performed by a fire protection professional engineer and reviewed by an independent fire protection professional engineer. The VA fire protection engineer may serve as the independent reviewer. | Note 2 - Demand Control Ventilation Incorporate demand-controlled ventilation sequence, if feasible, to control outdoor air based on carbon-dioxide concentration. Follow ASHRAE Standard 62.1 - 2016 (or latest approved edition) requirements for demand control ventilation. | Note 2 - Dedicated General Exhaust System (a) Exhaust System and Discharge Requirement. Provide a dedicated exhaust system to serve the Autopsy Suite. Locate the exhaust fan on the roof with the fan discharging above the highest point of the building. Provide a stack of sufficient height (minimum 10 ft. [3 m]) to discharge air at 3,500 fpm [18 m/s]. Follow the recommendations of the dispersion analysis to ensure that exhaust air does not enter outside air intakes, operable windows and other openings. Mount the fan bearings outside the airstream and monitor the fan status at the ECC. (b) Exhaust Ductwork. Maintain exhaust ductwork under negative pressure. Provide an airflow control valve to ensure accurate exhaust air volumetric flow. Provide an alarm locally and at the ECC to report air flow disruption. | Note 2 - Fume Hoods and Biological Safety Cabinets. Coordinate exhaust needs with the laboratory equipment (fume hoods and biological safety cabinets). Room noise levels can be increased by NC 5 for laboratories equipped with fume hoods and/or biological safety cabinets. | Note 2 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on the VA Cardio Vascular Laboratory Service Design Guide dated November 29, 2011. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 2 - Listed Rooms and Their Names. Listed rooms, their names and codes are based on information in the various Design Guides and VA PG18-9. | Note 2 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 2 – Energy Recovery System A central laundry presents many opportunities for energy recovery. (a) Hot exhaust from dryers and ironers can be used to preheat incoming domestic water prior to going to water heaters. (b) Hot exhaust from ironers can be recirculated into dryers and ironers. (c) Waste water from washer extractors can be used to preheat incoming domestic cold water. (d) Recover high pressure condensate flash steam from laundry equipment and reuse in domestic water heaters or in space heating. (e) Whenever using dryer and ironer exhaust provide lint filters in exhaust air stream. Provide instrumentation to alarm when filters are dirty. (f) Do not recirculate dryer exhaust into dryers as it will inhibit drying due to the moisture content of the air. | Note 2 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on the VA Dental Service Design Guide dated June 2014. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 2 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 2 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 2 - Exhaust System Provide a general or special exhaust system (NFPA 96) when the Dining Area (Cafeteria) is a standalone facility using a canopy and/or a range hood. Coordinate the exhaust air requirement with the kitchen consultant, drawings, and equipment catalogue cuts. | Note 2 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 2 - Makeup Air Requirements. Any air handling unit serving the EEG Laboratory spaces need not be a 100% outside air system, however, the system must have adequate outside air flow to match the exhaust requirement of all spaces served plus additional air flow for overall space pressurization, or the minimum required outside air of all the spaces served whichever is greater. | Note 2 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 2 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on VA PG18-9 Chapter 233 Eye Clinic, Revised October 03, 2016. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 2 - General Exhaust System Provide a general exhaust system to serve adjoining support spaces (examples: toilets, locker rooms, HAC, etc.). | Note 2 - Listed Rooms and Their Names. Listed rooms, their names and codes are based on information in the various Design Guides and VA PG18-9. | Note 2 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 2 - Dedicated Air-Handling Unit A dedicated air-handling unit is required if the AHU serving Infectious Isolation and other spaces is not capable of operating at 100% OA during emergency epidemic mode, or if the AHU does not meet the requirements of the hours of operation and filtration. | Note 2 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 2 - Fume Hoods and Biological Safety Cabinets Coordinate exhaust needs with the laboratory equipment (fume hoods and biological safety cabinets). Room noise levels can be increased by NC 5 for laboratories equipped with fume hoods and/or biological safety cabinets. | Note 2 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 2 - Dedicated Air-Handling Unit A dedicated air-handling unit is required if the AHU serving Inpatient MH and other spaces is not capable of operating at 100% OA during emergency epidemic mode, or if the AHU does not meet the requirements of the hours of operation and filtration. | Note 2 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on the VA Mental Health Facilities Design Guide dated December of 2010 and Revised August of 2014. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 2 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on the VA Mental Health Facilities Design Guide dated December of 2010 and Revised August of 2014. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 2 - Emergency Epidemic Air-Handling Unit (a) Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. (b) Minimum of 50% of the hospital Inpatient Nursing Units (WARDs) should be provided with AHUs capable of operating with 100% OA during emergency epidemic mode. For hospitals with less than 3 Inpatient Nursing Units, ALL AHUs serving the 3 or fewer Inpatient Nursing Units should be equipped with 100% OA capability for use during emergency epidemic mode. See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 2 - Unit Location and Type Locate all units in a dedicated mechanical room adjacent to the computer room. All units shall be floor- mounted. For new installations and major renovations, do not locate units in the computer room. Units must be designed for data processing applications. See VA specification 23 81 23, Computer Room Air Conditioners, for additional information. | Note 2 - Standby Capacity Provide N+1 computer room air-conditioning units. N = Number of units in operation required to meet the load and 1 is the standby unit of capacity equal or greater than the largest of the N units. | Note 2 - Makeup Air Requirements Any air handling unit serving the listed spaces need not be a 100% outside air system, however, the system must have adequate outside air flow to match the exhaust requirement of all spaces served plus additional flow to maintain the entire area positive with respect to the outside or the minimum required outside air of all the spaces served whichever is greater. | Note 2 - USP <797> Pharmaceutical Compounding - Sterile Preparations (CSP) and USP <800> Hazardous Drug Handling In Health Care Settings Per USP <797>, compounding of sterile products (hazardous or non-hazardous) shall be accomplished in a clean room environment. The designer shall be familiar with the environmental requirements specified in USP <797> to ensure compliance . In the Room Data Sheets for hazardous and non-hazardous clean rooms, terminology is defined. Per USP <800> storage and handling of hazardous drugs in a health care setting shall take place in spaces protected by negative pressure differentials. The designer shall be familiar with the environmental requirements specified in USP <800> to ensure compliance. | Note 2 - Emergency Epidemic Air-Handling Unit (a) Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 2 - Listed Rooms and Their Names Room names shown in the attached Room Data Sheets are based on the VA Polytrauma Rehabilitation Center Design Guide dated December 2014. See other sections of Chapter 6 for the miscellaneous and support rooms, such as, Housekeeping Aide's Closet (HAC), Attic Space, Crawl Space (Pipe Basement), Exterior Stairs, Mechanical/Electrical Rooms, etc. | Note 2 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on the VA Pulmonary Medicine Service Design Guide dated November 29, 2011. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 2 - Listed Rooms and Their Names. Listed rooms, their names and codes are based on information in the various Design Guides and VA PG18-9. | Note 2 - Listed Rooms and Their Names. Listed rooms, their names and codes are based on information in the various Design Guides and VA PG18-9. | Note 2 - Listed Rooms and Their Names. Listed rooms, their names and codes are based on information in the various Design Guides and VA PG18-9. | Note 2 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 2 - HVAC System Details and Controls The HVAC system selection shall be project specific - either a chilled water or direct-expansion (DX) system. (a) Chilled Water System. Provide a modulating chilled water control valve. (b) DX System. Provide at least two independent refrigeration circuits, if available for the required capacity. | Note 2 - General Coordination Coordinate equipment heat gain and utility requirements with the selected equipment. The abator is supplied with the ETO Sterilizer. Mechanical drawings shall indicate duct, pipe and utility connections. | Note 2 - Air Handling Unit System Features (a) Occupied/Unoccupied Modes. Provide two-position (occupied/unoccupied), pressure-independent, supply air terminal units and matching return air terminal units. (b) Variable Speed Drives. Provide variable speed drives for the supply and return air fans to adjust the fan speeds in unison during all modes of operation while still maintaining the design minimum outside air volume. (c) Coil Fins. Provide copper fins for ALL coils (pre-heat, cooling, and terminal reheat coils) at ALL locations. Copper fins possess anti-microbial property and anti-corrosive property that is useful in resisting corrosion in high-humidity locations and locations with industrial pollution. | Note 2 - Number of Air-Handling Units. (a) Provide two separate air-handling units, one to meet the lower indoor design temperature, 65 F [18 C], for the Animal Surgical Suite and Rabbit Holding Area and another unit to serve the Animal Holding Areas and Associated Spaces for which the indoor design temperature ranges from 72 F [22 C] to 77 F [25 C]. (b) Due to the lower space temperatures and humidity requirements in the animal surgery room a separate unit or supplemental cooling may be required. The supply temperature of chilled water (if connecting to an existing plan) shall be considered to ensure surgery conditions can be maintained. (c) For smaller facilities with few spaces requiring lower (65 F [18 C]) indoor temperature, dedicated, re-circulatory terminal cooling units can provide supplementary cooling in lieu of a dedicated air-handling unit. | Note 2 - Minimum Outdoor Air Unit See individual Room Data Sheets for required outdoor air changes. | Note 2 - Listed Rooms and Their Names Listed rooms, their names and codes are based on information in the various Design Guides and VA PG18-9.
Note 3 | Note 3 - Design Details (a) Upon activation of the smoke evacuation system, the Atrium AHU shall operate in 100% outdoor air mode. Provide an additional make-up air system if the required smoke removal volume is greater than the Atrium AHU supply air volume. The make-up air system shall be complete with fan, MERV 7 filter, and a heating coil. (b) Size the heating capacity to maintain 50 F [10 C] minimum space temperature in the smoke evacuation mode. For 32 F [0 C] and lower ambient temperatures, design the heating system with freeze protection measures. | Note 3 - Relative Humidity Control See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Special Exhaust System Provide a special exhaust system(s) to serve fume hoods and/or biological safety cabinets included in the project-scope. | Note 3 - AHU System Configuration. (a) The system configuration (CV or VAV) shall be project specific. Applications involving multiple hoods, selected to maintain fixed face velocity at varying sash positions, are ideally suited for a variable air volume system. Such VAV systems are designed to meet the simultaneous, but at times differing, needs of the room cooling load and equipment exhaust. The control system shall be designed to provide dynamic interaction between the equipment exhaust and general systems while still maintaining a constant "offset" (make-up air) from the adjoining corridor for negative air balance. (b) Use of low flow fume hoods shall be evaluated and compared to the VAV system. | Note 3 - Humidity Control See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Dedicated Air-Handling Unit A dedicated air-handling unit is required if the AHU serving CLC and other spaces is not capable of operating at 100% OA during emergency epidemic mode, or if the AHU does not meet the requirements of the hours of operation and filtration. | Note 3 – Special Exhaust Systems Exhaust all air in soiled receiving through exhaust grills above washer / extractor loading door to remove contaminated air and to create directional air flow on the contaminated side. Dryers and ironers must be exhausted and must have makeup air systems. See energy recovery note 2. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on VA PG18-9 Chapter 316 Dialysis Center, Revised October 03, 2016. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 3 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on the VA Digestive Disease Endoscopy Service Design Guide dated November 29, 2011. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 3 - Air Balance Maintain the Dining Area (Cafeteria) under negative air balance with respect to the adjoining spaces. | Note 3 - Dedicated Air-Handling Unit A dedicated air-handling unit is required if the AHU serving Domiciliary and other spaces is not capable of operating at 100% OA during emergency epidemic mode, or if the AHU does not meet the requirements of the hours of operation and filtration. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - General Exhaust System Exhaust the spaces associated with the Emergency Department either by a dedicated or a common exhaust system (examples: toilets, locker rooms, HAC, etc.) | Note 3 - Makeup Air Requirements Any air handling unit serving the Eye Clinic spaces need not be a 100% outside air system, however, the system must have adequate outside air flow to match the exhaust requirement of all spaces served plus additional air flow to ensure overall area is positive or the minimum required outside air of all the spaces served whichever is greater. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Number of Air Handling Units The number of air handling units to be used shall depend on a study of the differences in required space conditions amongst the different types of imaging systems being provided, the expected operating hours, project budget, and physical space constraints of the project. | Note 3 - Constant Volume Constant volume air flow control valves shall be used to maintain constant air flow as well as constant air flow differential between adjacent spaces. | Note 3 - Grease Hood Exhaust System Provide a dedicated exhaust system to remove grease-laden air in accordance with NFPA 96. The design shall also follow the following code requirements: (a) Discharge exhaust per dispersion analysis recommendations. (b) Maintain at least 40 in [1,000 mm] between the roof surface and exhaust air outlet. (c) Do not install fire dampers, volume dampers, and turning vanes in the exhaust duct. Avoid excessive horizontal runs and install access doors at each turn for grease removal. Slope duct towards the hood. (d) Do not install exhaust duct in the shaft carrying environmental ducts (NFPA 90A). (e) Provide exhaust system and AHU with controls to reduce exhaust and make-up air flows when the cooking equipment is turned off. | Note 3 - AHU System Configuration (a) The system configuration (CV or VAV) shall be project specific. Applications involving multiple hoods, selected to maintain fixed face velocity at varying sash positions, are ideally suited for a variable air volume system. Such VAV systems are designed to meet the simultaneous, but at times differing, needs of the room cooling load and equipment exhaust. The control system shall be designed to provide dynamic interaction between the equipment exhaust and general systems while still maintaining a constant "offset" (make-up air) from the adjoining corridor for negative air balance. (b) Use of low flow fume hoods shall be evaluated and compared to the VAV system. | Note 3 - Air Balance Maintain lobby at positive air balance with respect to the vestibule. Calculate exfiltration to maintain at least 0.02 Inch WC. | Note 3 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on the VA Mental Health Facilities Design Guide dated December of 2010 and Revised August of 2014. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Telephone Equipment Room and Facility Management Service Provide similar air-conditioning systems for the Telephone Equipment Room and the Facility Maintenance Service (FMS). Standby units can be shared between IT (Information Technology), FMS, and Telephone Equipment Room if a common mechanical room is provided. Ensure coordination with the Office of Information and Technology (OIT) Design Guide for additional information and design criteria. | Note 3: - Heating Not Required Where the room is located without an exterior wall or where the heat load due to electronic equipment exceeds the room’s heating load do not provide heating with this system. Ensure VAV minimum flow is low enough so as not to overcool the room. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Air-Handling Unit An air-handling unit serving clean rooms must address the special HVAC needs of providing Final MERV 17 (HEPA) filters, extended hours of operations, and lower space temperature (68 F [20 C] compared to 75 F [24 C] for all other spaces). The Pharmacy suite AHU shall not serve any patient areas. Provide terminal HEPA filters at clean room ceiling supply diffusers, equipped with static pressure port and DOP port for testing. | Note 3 - Listed Rooms and Their Names Room names shown in the attached Room Data Sheets are based on the VA Polytrauma Rehabilitation Center Design Guide dated December 2014. See other sections of Chapter 6 for the miscellaneous and support rooms, such as, Housekeeping Aide's Closet (HAC), Attic Space, Crawl Space (Pipe Basement), Exterior Stairs, Mechanical/Electrical Rooms, etc. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Makeup Air Requirements Any air handling unit serving the pulmonary medicine services spaces need not be a 100% outside air system, however, the system must have adequate outside air flow to match the exhaust requirement of all spaces served plus additional flow to maintain the area positive relative to the outside, or the minimum required outside air of all the spaces served whichever is greater. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 3 - Listed Rooms and Their Names Room names shown in the attached Room Data Sheets are based on PG-18-9 Chapter 104 Spinal Cord Injury / Disorders Center See other sections of Chapter 6 for the miscellaneous and support rooms, such as, Housekeeping Aide's Closet (HAC), Attic Space, Crawl Space (Pipe Basement), Exterior Stairs, Mechanical/Electrical Rooms, etc. | Note 3 - Suggested Control Sequences (a) Unoccupied Mode. The system shall cycle (on/off) with the outdoor air damper closed to maintain a night-setback temperature at 60 F [16 C]. (b) Purge Cycle. A dedicated exhaust fan shall operate intermittently during occupied mode to flush smoke-laden air outdoors. | Note 3 - General Exhaust System Provide a dedicated, general exhaust system for the spaces identified in the Room Data Sheets. Provide the main general exhaust system with N+1 fan capability and controls to bring on the lag fan upon lead fan failure. Interlock AHU fan with exhaust air flow. | Note 3 - Emergency Epidemic Air-Handling Unit Refer to Par 6.4 DESIGNATED EMERGENCY EPIDEMIC AIR-HANDLING UNITS for additional specific requirements, including 100% OA delivery during emergency mode. | Note 3 - Special Acoustical and Vibration Needs. Animals are susceptible to low-frequency rambling noise and vibrations. Implement the recommendations of the acoustic analysis in the HVAC system and building design. Address the noise and vibration transmitted between the floors and the cage washing equipment and the animal holding areas by using acoustic blankets and/or tiles. | Note 3 - Control Strategy See Chapter 3 for the recommended ventilation air control strategy. | Note 3 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity.
Note 4 | Note 4 - Relative Humidity Control See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 4 - General Exhaust System Exhaust the spaces associated with the Auditorium and Theater either by a dedicated or a common exhaust system (examples: toilets, HAC, etc.). | Note 4 - Relative Humidity Control See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 4 - General Laboratory. General Laboratory or "Dry Laboratory" is defined as a space without hoods or biological safety cabinets and chemicals are not used within the space. Generally used for research activities, these laboratories contain electronic equipment. Room air can be returned back to the unit, but the cost-effectiveness of doing so when using 100% outdoor air units shall be evaluated before doing so. | Note 4 - Enhanced Air Filtration (a) During Emergency Epidemic use enhanced after-filters as noted above. (b) Size the AHU supply and return/relief fan motors to compensate for the additional air pressure drop due to enhanced filtration application. (c) The AHU filter section shall be configured to accommodate installation of enhanced after-filters during Emergency Epidemic. (d) Before switching from emergency to normal operation mode, replace all air filters and thoroughly clean and disinfect AHU interior surfaces. |  | Note 4 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on the VA Community Living Center Design Guide dated June 2011. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 4 - General Exhaust Systems Provide general exhaust above washer extractor unloading doors to help control heat and humidity. |  | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 4 - Listed Rooms and Their Names Listed rooms, their names, codes, and design conditions found in the RDS sheets that follow this air handling unit are based on VA PG18-9 Chapter 312 Domiciliary, Revised October 03, 2016. See other RDS sheets for general purpose support and clinical spaces found in multiple areas of medical facilities. | Note 4 - Enhanced Air Filtration (a) During Emergency Epidemic use enhanced after-filters as noted above. (b) Size the AHU supply and return/relief fan motors to compensate for the additional air pressure drop due to enhanced filtration application. (c) The AHU filter section must be configured to accommodate installation of enhanced after-filters during Emergency Epidemic. (d) Before switching from emergency to normal operation mode, replace all air filters and thoroughly clean and disinfect AHU interior surfaces. | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. |  |  | Note 4 -MRI (Magnetic Resonance Imaging) Unit (a) Reference Document - MRI Design Guide published by the VA Office of Construction and Facilities Management: This Publication contains valuable information about the space layout, equipment list, exhaust system and utility requirements. A design guide plate for each room shows tentative room dimensions and equipment layout. (b) Coordination - Capacity and configuration of the MRI Unit varies by manufacturer. Coordinate with the project specific MRI vendor is mandatory. Coordinate vibration isolation requirement of AHU(s) sited in proximity to the MRI scanner. (c) RF Shielding - For HVAC ducts and pipes penetrating RF shielding of the MRI Scanning Room, coordinate penetration requirements with MRI system manufacturer, RF shield vendor, and architectural discipline. (d) Other HVAC Related Issues - MRI chilled water system, and MRI quench vent system design shall be closely coordinated with the specific MRI system being provided. Ensure the coordination in the documents takes into consideration all MRI system provided equipment to be installed by the building contractor. | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 4 - Make-Up Air Hood (Grease Hood Exhaust) Make-up air hood is permitted if proven economically viable. Past experience has shown that the initial and recurring costs associated with the make-up air system and the discomfort experienced by the kitchen staff due to the proximity of marginally tempered make-up air makes the make-up air hood system as a less desirable alternate. | Note 4 - General Laboratory General Laboratory or "Dry Laboratory" is defined as a space without hoods or biological safety cabinets and chemical are not used within the space. Generally used for research activities, these laboratories contain electronic equipment. Room air can be returned back to the unit, but the cost-effectiveness of doing so when using 100% outdoor air units shall be evaluated before doing so. | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 4 - Enhanced Air Filtration (a) During Emergency Epidemic use enhanced after-filters as noted above. (b) Size the AHU supply and return/relief fan motors to compensate for the additional air pressure drop due to enhanced filtration application. (c) The AHU filter section shall be configured to accommodate installation of enhanced after-filters during Emergency Epidemic. (d) Before switching from emergency to normal operation mode, replace all air filters and thoroughly clean and disinfect AHU interior surfaces. | Note 4 - Enhanced Air Filtration (a) During Emergency Epidemic use enhanced after-filters as noted above. (b) Size the AHU supply and return/relief fan motors to compensate for the additional air pressure drop due to enhanced filtration application. (c) The AHU filter section must be configured to accommodate installation of enhanced after-filters during Emergency Epidemic. (d) Before switching from emergency to normal operation mode, replace all air filters and thoroughly clean and disinfect AHU interior surfaces. | Note 4 - Enhanced Air Filtration (Not applicable to Emergency Epidemic AHUs) (a) During Emergency Epidemic use enhanced after-filters of MERV 16A. (b) Size the AHU supply and return/relief fan motors to compensate for the additional air pressure drop due to enhanced filtration application. (c) The AHU filter section mustbe configured to accommodate installation of enhanced after-filters during Emergency Epidemic. (d) Before switching from emergency to normal operation mode, replace all air filters and thoroughly clean and disinfect AHU interior surfaces. | Note 4 - Raised Floor Protection Provide an under floor, water leak detection system and a smoke detector to detect smoke and initiate corrective actions with alarms. | Note 4 - Recommended Option 1 For rooms located within areas served by central air handling units operating on normal and emergency power provide one VAV terminal from one unit and a second VAV terminal from a second unit (N+1). Locate terminals outside the room it serves. Provide hot water reheat or resistance heating to each terminal if heating is needed. | Note 4 - Enhanced Air Filtration (a) During Emergency Epidemic use enhanced after-filters as noted above. (b) Size the AHU supply and return/relief fan motors to compensate for the additional air pressure drop due to enhanced filtration application. (c) The AHU filter section must be configured to accommodate installation of enhanced after-filters during Emergency Epidemic. (d) Before switching from emergency to normal operation mode, replace all air filters and thoroughly clean and disinfect AHU interior surfaces. | Note 4 - Chilled Water Chilled water shall be available uninterrupted and on demand. A dedicated chiller connected to emergency power shall be considered if the central plant is not equipped with emergency power. | Note 4 - Indoor Design Conditions (Temperatures - Bedrooms and Isolation Rooms) Temperature tolerance for heating and cooling modes is +/- 1.0 F [0.6 C]. | Note 4 - Enhanced Air Filtration (a) During Emergency Epidemic use enhanced after-filters as noted above. (b) Size the AHU supply and return/relief fan motors to compensate for the additional air pressure drop due to enhanced filtration application. (c) The AHU filter section must be configured to accommodate installation of enhanced after-filters during Emergency Epidemic. (d) Before switching from emergency to normal operation mode, replace all air filters and thoroughly clean and disinfect AHU interior surfaces. | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. |  |  |  | Note 4 - Indoor Design Conditions (Temperatures - Bedrooms and Isolation Rooms) Temperature tolerance for heating and cooling modes is +/- 1.0 F [0.6 C] | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 4 - Wet Exhaust System Provide a dedicated (space) exhaust system for the Manual Equipment Wash and Automatic Cart Washer Rooms. Detail the duct system installation to prevent and / or drain low spots in the ductwork which may accumulate water. | Note 4 - Humidifier (a) Provide unit-mounted steam humidifier. The preferred location for the dispersion tubes is between the preheat coil and cooling coil. This section of the air handling unit must have a properly slopped stainless steel drain pan to drain out excess moisture. The humidifier controls must be routed through a high limit humidistat set at a maximum of 80% RH. (b) See paragraph 6.5.1.1 for humidifier capacity. | Note 4 - High-Limit Temperature Controls. (a) Room Air Temperature Control - Animal Holding and Serving Areas. Each room temperature sensor shall be equipped with a high-limit sequence to disable the room air terminal unit when the temperature exceeds the design set point by 5 F [3 C] and initiate a visible local alarm and a remote alarm at the EEC. (b) Supply Air Temperature Control - Air Handling Units. Each supply air temperature sensor shall be equipped with a high-limit sequence to disable the air-handling unit and initiate a visible alarm at the serving area and a remote alarm at the ECC, if the supply air temperature exceeds the set point by 10 F [6 C]. | Note 4 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity.
Note 5 |  |  |  | Note 5 - Nuclear Laboratory. Nuclear Medicine Laboratory is included in the dedicated air-handling system for the Imaging Series. |  |  | Note 5 - Relative Humidity Control See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 5 – Load Calculations Consult laundry equipment manufacturer for heat dissipation off washer extractors, dryers and ironers and ensure the information provided includes heat given off by linen as it is transported from machine to machine and while it is stored. |  |  |  |  | Note 5 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. |  | Note 5 - Post Pandemic Mode Before switching from pandemic emergency mode to normal mode, change all filters and sterilize air handling unit. Method of sterilization will be dependent on the pathogen or event. In addition to AHU section doors, provide access doors in connected ductwork that allows access to dampers and other components. If the return or exhaust fans are external, provide access doors to allow access to fans, dampers, and duct connected to AHU. | Note 5 - Enhanced Air Filtration (a) During Emergency Epidemic use enhanced after-filters as noted above. (b) Size the AHU supply and return/relief fan motors to compensate for the additional air pressure drop due to enhanced filtration application. (c) The AHU filter section shall be configured to accommodate installation of enhanced after-filters during Emergency Epidemic. (d) Before switching from emergency to normal operation mode, replace all air filters and thoroughly clean and disinfect AHU interior surfaces. |  |  | Note 5 - Radiology Service (a) Reference Document - Radiology Service Design Guide Published by the VA Office of Construction and Facility Management: This publication contains valuable information about the space layout, equipment list, and utilities requirements. A design guide plate for each room shows tentative room dimensions and the equipment layout. (b) Shielded Walls and Ceilings - For HVAC ducts and pipes penetrating shielded walls and ceilings, ensure coordination with the architectural discipline and provide treatment as specified by the equipment manufacturer and medical physicist. |  | Note 5 - General Exhaust System (Optional) Provide a dedicated exhaust system to capture heat over refrigeration condensing units, plate warmer, mixer, etc. Factory or field-installed installed canopy hoods may be required. | Note 5 - Nuclear Laboratory Nuclear Medicine Laboratory is included in the dedicated air-handling system for the Imaging Series. | [5 empty] | Note 5 - Air Distribution System Coordinate the location and type of supply and return air distribution systems with the building design as numerous configurations outlined in the OIT Design Guide are considered as acceptable configurations. | Note 5 – Option 2 If only one central air handling unit operating on normal and emergency power is convenient to the space, provide one VAV terminal from that system as in Options 1 and provide one wall mounted ductless split DX heat pump or cooling only unit. Install wall unit with secondary condensate drain pan and monitor water in the secondary pan. In locations where humidification is required provide either a self-contained humidifier using plant steam or an electric steam generator. |  | Note 5 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 5 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. |  | Note 5 - Enhanced Air Filtration (a) During Emergency Epidemic use enhanced after-filters as noted above. (b) Size the AHU supply and return/relief fan motors to compensate for the additional air pressure drop due to enhanced filtration application. (c) The AHU filter section must be configured to accommodate installation of enhanced after-filters during Emergency Epidemic. (d) Before switching from emergency to normal operation mode, replace all air filters and thoroughly clean and disinfect AHU interior surfaces. |  |  |  | Note 5 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. |  | Note 5 - Wet Exhaust System (Automatic Cart Wash Equipment) Provide a dedicated (equipment) exhaust system for the Automatic Cart Wash Equipment. The system capacity shall be based on the actual selected equipment. Prevent and/or drain low points in the duct system which may accumulate water during operation. | Note 5 - Ductwork (a) Flexible Duct. Use of flexible duct is NOT permitted in the distribution system. (b) Use of acoustic lining in ducts, air terminals, sound attenuators, and other equipment is prohibited. Refer to Chapter 2, paragraph 2.3.1.2 for more information. (c) Duct Pressure Classification. Calculate the duct pressure classification for the supply air ductwork from the air-handling unit to the air terminal units. With terminal HEPA filters on the downstream side of each terminal unit, the expected pressure classification may range from 3 in [747 Pa] to 4 in [996 Pa]. (d) Duct Velocity. All ductwork shall be low-velocity type with maximum duct velocity not exceeding 1,500 fpm [8 m/s]. Provide lower velocity if recommended by the acoustic analysis. (e) Duct Fabrication. All ductwork shall be fabricated from galvanized steel with the following exception: For Operating Rooms, Cystoscopy Rooms and Clean Core, supply air ductwork and distribution system shall be fabricated of stainless steel with welded joints downstream of the final filters. | Note 5 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. (c) Provide local and ECC alarms as required for the space functions.
Note 6 |  |  |  | Note 6 - Relative Humidity Control See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | [14 empty] | Note 6 - Nuclear Medicine (a) Reference Document. Radiology Service Design Guide Published by the VA Office of Construction and Facility Management: This publication contains valuable information about the space layout, equipment list, and utilities requirements. A design guide plate for each room shows tentative room dimensions and the equipment layout. (b) Exhaust Systems - Provide a special exhaust system(s) for fume hoods and biological safety cabinets. Coordinate hood locations and sizes with the architectural discipline. For radioisotope hoods, coordinate the need for HEPA filters or Carbon Filters or both or no filters with the VA Safety Officer. (c) Shielded Walls and Ceilings - For HVAC ducts and pipes penetrating shielded walls and ceilings, ensure coordination with the architectural discipline and provide treatment as specified by the equipment manufacturer and medical physicist. |  | Note 6 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 6 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | [5 empty] | Note 6 - Automatic Controls Provide a local control panel in the Main Computer Room displaying temperature, RH and unit status for each AHU. Provide an open-protocol, BACnet interface between the control panel furnished with the AHU unit and the central ECC system. Controls shall be protected by UPS. | Note 6 – Option 3 If there are no convenient central air handling units operating on emergency power nearby provide two separate wall mounted ductless split DX heat pumps with the same provisions as in option 2 including a humidifier. Provide air from any nearby system for ventilation and do not return to the air handling unit used. |  | Note 6 - Enhanced Air Filtration (a) During Emergency Epidemic use enhanced final-filters as noted above. (b) Size the AHU supply and return/relief fan motors to compensate for the additional air pressure drop due to enhanced filtration application. (c) The AHU filter section shall be configured to accommodate installation of enhanced final-filters during Emergency Epidemic. (d) Before switching from emergency to normal operation mode, replace all air filters and thoroughly clean and disinfect AHU interior surfaces. | [8 empty] | Note 6 - Ethylene Oxide (ETO) Exhaust System (a) General - New Construction and Major Renovations of the SPS Department. Per VHA (Veterans Health Administration) Directive, under processing and concurrence, the following measures shall be implemented: For all new construction and major renovations, provide an Abator for each Ethylene Oxide (ETO) sterilizer to convert the ETO exhaust into water vapor and carbon-oxide. Per Directive in all existing ETO sterilizer installations, abators shall be installed by 2015. No ETO sterilizers shall be used without abators after 2015. (b) Abator is a pollution control device. Vent line from each ETO sterilizer is connected to its own abator to split ethylene-oxide into water vapor and carbon-oxide by an exothermic reaction. Per VHA direction, each sterilizer shall be equipped with its own abator to avoid a single point of failure and facilitate on-line maintenance. (c) Exhaust System. The dedicated exhaust system serving the ethylene oxide sterilizer installation shall include exhaust through the sterilizer room, abator, and the flammable storage cabinet required to house the ETO canisters. (d) ETO Sterilizer Room Exhaust. Exhaust through or over the sterilizer by an integral plenum is not required, as the VA Standard Operating Procedure permits opening of the sterilizer door only after the specified time limit has expired at the end of each operating cycle. Provide ceiling-mounted exhaust register over the sterilizer door to exhaust the room at 10 air changes per hour. (e) Exhaust through the Abator. Each abator admits 50 cfm [24 L/s] room air through its intake nozzle and discharges it through its exhaust nozzle at very high temperature, approximately at 480 F [250 C]. Room air is mixed at the rate of 150 cfm [70 L/s] with the hot air discharge discharged by the abator to dilute the hot air. This is accomplished by a three-way mixing nozzle supplied by the equipment manufacturer. (f) Exhaust through the Flammable Storage Cabinet. Admit room air into the cabinet through the cabinet doors and connect the cabinet exhaust nozzle to the exhaust system. Ensure that enough air is exhausted to create -0.06 in [-15 Pa] negative air pressure. The approximate nozzle size is 4 in [100 mm] and the exhaust air volume is 40 to 50 cfm [19 to 24 L/s]. (g) Abator Vent Pipe. Each abator is equipped with its own vent pipe, operative during emergency only when the intended chemical reaction to break the ETO into water and CO2 does not materialize. Coordinate vent pipe size, material, fittings, and equivalent length limitation with the ETO manufacturer. Coordinate vent termination details with the equipment manufacture. (h) Exhaust Fan and Ductwork. Provide a non-ferrous, spark-proof construction centrifugal fan with a backward inclined wheel. The fan motor shall be mounted outside the exhaust air stream. Maintain complete exhaust air ductwork under negative air balance. Provide an airflow control valve to ensure accurate air balance. Locate the fan and abator vent exhaust pipe at least 25 ft [8 m] from any outdoor air intake, unsealed doors and windows, driveways, and walkways. Modify the discharge requirements if so recommended by the dispersion analysis. | Note 6 - Final Filters Final filters shall be provided downstream of ALL air terminal units, served by the Surgical Suite AHU. For spaces other than Operating and Cystoscopy Rooms, the use of a final HEPA filter ensures a balanced pressure drop at all air terminal units. | Note 6 -Local Alarms. All local alarms shall be visible type, such as, rotating red light, as audible alarms disturb animals and create panic situations. All remote alarms at the ECC shall initiate an audible device and a printed message. High / low temperature and humidity alarms are required in all animal holding areas.
Note 7 |  |  |  | Note 7 - Local Heat Recovery Where compatible with electronic laboratory equipment provide local snorkel indirect connections to remove heat directly from the laboratory equipments cooling fan into the general exhaust system. | [14 empty] | Note 7 - Radiation Therapy Service (a) Reference Document - Radiology Service Design Guide Published by the VA Office of Construction and Facility Management: This publication contains valuable information about the space layout, equipment list, and utilities requirements. A design guide plate for each room shows tentative room dimensions and the equipment layout. (b) Shielded Walls and Ceilings - For HVAC ducts and pipes penetrating shielded walls and ceilings, ensure coordination with the architectural discipline and provide treatment as specified by the equipment manufacturer and medical physicist. |  | Note 7 - Wet Exhaust System Provide a dedicated exhaust system to capture and remove moisture over pot/pan washing areas, dishwashers, steam kettles, steamers and high-pressure cookers. Use field-installed or integral hoods furnished by the equipment manufacturer. | Note 7 - Local Exhaust Where compatible with electronic laboratory equipment provide local snorkel indirect connections to remove heat directly from the laboratory equipments cooling fan into the general exhaust system. | [5 empty] | Note 7 - Space Pressurization Provide environmental air from a dedicated or a common adjoining air-handling unit to pressurize the space. Do not return air to the adjoining air handling unit. | Note 7 - Automatic Controls Ductless split systems and stand-alone humidifier shall work on their own integral controls. Provide space temperature sensor, space humidity sensor, auxiliary drain pan moisture sensor (not float switch) and supply air temperature sensors on all DX units and /or VAV terminals and connect these to the central ECC system for trending and alarm purposes. | [10 empty] | Note 7 - Air Distribution Requirements (a) Air distribution system design is vital to ensure contamination control. The design should demonstrate the directions and magnitude of the supply, exhaust, and make-up air flows. Provide automatic airflow control valves, as required, to accomplish the design objective. It is vital to ensure that the supply air inlets and exhaust air outlets are judiciously located. (b) Strategically locate exhaust grills, or where advantageous provide local capture exhaust hoods at high humidity and / or high heat locations. For example above the inlet and outlet sides of washer disinfectors and at the loading end of steam sterilizers. (c) See Sterile Processing Service Air Flow Relationships diagram next page. | Note 7 - Air Distribution (Operating Rooms and Cystoscopy Rooms) (a) Supply air through laminar flow diffusers in a central array located above and around the surgical field. (b) Return Air. Provide at least two return air inlets, fabricated from aluminum, to pick-up return air at approximately 7 in [175 mm] above the floor level. The inlets shall be located diagonally across from one another. (c) Supply Air Terminal Units. All supply air terminal units shall be 100% fabricated from stainless steel and without integral acoustic lining. (d) Return Air Terminal Units. All return air terminal units can be conventional variable air volume boxes or airflow control valves (AFCV) and without acoustical lining. | Note 7 -Chilled Water. If uninterrupted supply of chilled water is not available on demand from the central chilled water plant, provide dedicated air-cooled chillers (N+1) connected to an emergency power supply. The air-cooled machines will facilitate easy start in mild weather. Dedicated chillers may also be required if the central chilled water plant cannot deliver chilled water at the lower temperature required to maintain 65 F [18 C] at 55% RH for the surgery and laboratory areas, etc.
Note 8 | [18 empty] | Note 8 - Indoor Design Conditions (a) Variance from This Manual - Indoor design conditions may vary from Room Data Sheets to meet the requirements of the selected equipment. (b) Relative Humidity - See paragraph 6.5.1.1 for: (1) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (2) Humidifier capacity. |  | Note 8 - Energy Recovery System or Return Air Based on the actual air balance and the life-cycle cost analysis, either return the "clean air" to the system or exhaust outdoors after passing through an enrgyy recovery system. Note that the use of an energy recovery system is not permitted with grease laden and wet air exhausts. | [6 empty] | Note 8 – Alarm Monitoring The central ECC system shall monitor space conditions and unit status and shall alarm the boiler plant operator or HVAC shop whenever temperature or humidity are out of tolerance, when water is in the under floor space, when water is in the HVAC secondary drain pan if one is provided, and when the computer room unit status is not normal. | Note 8 - Space Pressurization For options 2 and 3 provide environmental air from a dedicated or a common adjoining air-handling unit to pressurize the space. Do not return air to the adjoining air handling unit. | [10 empty] | Note 8 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | Note 8 - Air Distribution (All Other Spaces) (a) Supply, Return and Exhaust Air. Provide conventional overhead supply, return, and exhaust air ductwork with painted steel or aluminum air outlets and inlets. (b) Supply and Return Air Terminal Units. All supply air terminal units shall be fabricated from galvanized steel and shall be the standard product of the manufacturers. The return air terminal units can be conventional variable air volume boxes or airflow control valves (AFCV). | Note 8 - Temperature and Humidity. (a) All animal holding rooms shall be capable of housing all types of species. The HVAC system shall also be capable of maintaining the full range of requirements for all anticipated animal populations. The temperature range required to accommodate most commonly used research animals is 65 F [18 C] to 84 F [29 C]. The ranges do not represent acceptable fluctuation ranges. The fluctuation ranges shall be determined during the design with input from the COR and the researchers. (b) Room temperatures shall be maintained +/- 2 F [1 C] and +/- 5% RH.
Note 9 | [18 empty] | Note 9 - Design Documents The Room Data Sheets indicate generic requirements of various equipment in the Imagining Series. If the details of the selected equipment are not known when design documents are issued, provide a design based on information in the Room Data Sheets and based on an agreed vendor. The purpose is to provide a reasonable level of documentation for construction pricing and bidding. | [8 empty] | Note 9 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. (c) CRAC manufacturer's standards sequence is acceptable. | Note 9 – Alarm Monitoring The central ECC system shall monitor space conditions and unit status and shall alarm the boiler plant operator or HVAC shop whenever temperature or humidity are out of tolerance, when water is in the HVAC secondary drain pan if one is provided. and when any supply air temperature does not match what is required by room conditions. | [11 empty] | Note 9 - Temperature and Relative Humidity Controls (a) Room Temperature Control Provide individual room temperature control for Operating Rooms, Cystoscopy Rooms, and other spaces identified in the Room Data Sheets. Provide trend logging capability at the ECC in EXCEL type spreadsheet format. (b) Room Humidity Sensors Provide room humidity sensors for each Operating and Cystoscopy Room to measure and record the space relative humidity. While the space relative humidity is controlled by the cooling coil leaving dew-point temperature in the dehumidification mode and by the central humidifier in the humidification mode, the DDC control system shall poll the space relative humidity sensors to initiate the corrective actions: (b.1) Dehumidification Mode. The relative humidity is not directly controlled but maintained within the range by controlling the dew-point temperature between 47 F to 48 F [8 C to 9 C], based on the psychometric analysis at 66 F [19 C] and 55% RH with 60% RH as the high limit. Upon rise in relative humidity above 60%, initiate alarms (local visible and remote at the ECC) and project-specific corrective actions. (b.2) Humidification Mode. Upon drop in space relative humidity below 20%, measured by any space relative humidity sensor, the central humidifier shall be activated to maintain the set point. (b.3) Additional Information. See chapter 6 paragraph 6.4.1.1 for additional information. (c) Space Pressure Differential Control See chapter 6 paragraph 6.5.2 AIR BALANCE. | Note 9 - Redundancy. Requirements for N+1 redundancy shall be discussed with the project COR. This requirement will be dependent on the project scope. For stand alone research facilities the redundancy requirements identified in the NIH DRM shall be utilized. For research areas inside existing facilities the COR shall provide guidance.
Note 10 | [28 empty] | Note 10 - Relative Humidity See paragraph 6.5.1.1 for: (a) Indoor Design Relative Humidity for required high and low relative humidity control strategies. (b) Humidifier capacity. | [11 empty] | Note 10 - Special Chilled Water Requirement. Uninterrupted supply of chilled water (at the design chilled water supply temperature) shall be available on demand. In the event the central chilled water plant can not meet this requirement, provide a dedicated chiller (N+1) on emergency power. Provide cross connections between the central chilled water plant and the dedicated chiller(s) to ensure flexibility in operation.
Note 11 | [40 empty] | Note 11 - Filtration - Final-Filter (FF) (a) Final filters will not be required if the following conditions are met: 1. The After Filter in the AHU is changed from a MERV 14 filter to a MERV 17 filter (HEPA) and properly in-situ tested. (b) If final filters are used the following conditions shall be met: 1. Filter units shall be located outside the operating rooms and clean core and downstream of the terminal terminals. 2. The filter unit shall be designed and installed with all necessary hardware and accessibility to allow for in-situ DOP testing of HEPA filters. 3. All ductwork, and ductwork appurtenances and equipment in contact with supply air-stream downstream of the HEPA filters shall be made of stainless steel.
Note 12 | [40 empty] | Note 12 - Maximum Number of Operating Rooms Wherever practical the design shall include a maximum of 4 to 6 operating rooms per air handling unit. The purpose of this requirement is to improve the reliability of the surgical suite and to allow for future contingencies such as air handling unit replacements.